## Read me
Cable catalog review
Generated 2026-09-28 from the cable catalog in the Cable Tray Design app (2455 rows from 9 manufacturers).
Why this review is needed
The catalog was read automatically from the manufacturer PDFs. Automatic checks found rows whose values are impossible or unusual. 72 rows are excluded: they are hidden from cable selection until corrected. 298 rows need review: they can be selected but show a warning.
How to review a row
1. Open the sheet "Rows to review". Each line is one catalog cable and lists the problems found.
2. Open the PDF named under "Catalogue file" (in the pdfs folder) at the given page and find the cable. "Original text" shows what was read from the PDF.
3. In "Decision" (yellow), choose one:
correct: a value is wrong. Enter the right value in the "Correct …" columns; leave the others blank.
Rows marked "Conductor may be aluminium" usually need Correct conductor = Al (check the resistance or product code in the PDF).
accept: the row is right as it is (for example two genuine product variants).
exclude: the cable should not be offered.
4. Fill in "Note" (what you checked, e.g. "PDF p.20 shows 7.1 mm") and "Reviewed by". "Date" is filled with the import date if left blank.
5. Leave "Decision" blank for rows you did not check. Save the file and send it back.
A correction is checked again automatically. A row cannot be accepted while it has an impossible value: correct it or exclude it.
Weights that are not plausible are hidden rather than used; a weight does not change the tray size, only the reported tray load.
For the development team
Import the returned file with: npm run catalog:import-review -- path/to/catalog-review.xlsx (in the app folder), then run npm test.

## Rows to review
Row ID | Status | Problems found | Brand | Cable | Materials | Voltage | Standard | Code / variant | OD (mm) | Weight (kg/km) | Catalogue file | Page | Original text | Decision | Correct OD (mm) | Correct weight (kg/km) | Correct size (mm²) | Correct cores | Correct conductor (Cu/Al) | Note | Reviewed by | Date
alfanar-1345 | Needs review | Conductor may be aluminium: Weight of 1,410 kg/km is too light for copper conductors (about 1,867 kg/km) but fits aluminium (about 567 kg/km); the conductor may be aluminium. | alfanar | 3-core 70 mm² | Cu/PVC/SWA | 0.6/1 kV | IEC 60502-1 | A419PA1030GCB04IMR | 31.1 | 1410 | Alfanar cables.pdf | 33 | 70 sm 0.4430 0.5331 128 100 126 31.1 1410 A419PA1030GCB04IMR
alfanar-1347 | Needs review | Conductor may be aluminium: Weight of 2,490 kg/km is too light for copper conductors (about 3,200 kg/km) but fits aluminium (about 972 kg/km); the conductor may be aluminium. | alfanar | 3-core 120 mm² | Cu/PVC/SWA | 0.6/1 kV | IEC 60502-1 | A446PA1030GCB04IMF | 38.6 | 2490 | Alfanar cables.pdf | 33 | 120 sm 0.2530 0.3055 175 139 180 38.6 2490 A446PA1030GCB04IMF
alfanar-1354 | Needs review | Conductor may be aluminium: Weight of 2,685 kg/km is too light for copper conductors (about 3,378 kg/km) but fits aluminium (about 1,026 kg/km); the conductor may be aluminium. | alfanar | 4-core 95 mm² | Cu/PVC/SWA | 0.6/1 kV | IEC 60502-1 | A445PA1040GCB08IMF | 40.8 | 2685 | Alfanar cables.pdf | 33 | 95 sm 0.3200 0.3856 155 122 157 40.8 2685 A445PA1040GCB08IMF
alfanar-1355 | Needs review | Conductor may be aluminium: Weight of 3,190 kg/km is too light for copper conductors (about 4,267 kg/km) but fits aluminium (about 1,296 kg/km); the conductor may be aluminium. | alfanar | 4-core 120 mm² | Cu/PVC/SWA | 0.6/1 kV | IEC 60502-1 | A446PA1040GCB08IMF | 44.6 | 3190 | Alfanar cables.pdf | 33 | 120 sm 0.2530 0.3055 175 139 180 44.6 3190 A446PA1040GCB08IMF
alfanar-1356 | Needs review | Conductor may be aluminium: Weight of 3,820 kg/km is too light for copper conductors (about 5,334 kg/km) but fits aluminium (about 1,620 kg/km); the conductor may be aluminium. | alfanar | 4-core 150 mm² | Cu/PVC/SWA | 0.6/1 kV | IEC 60502-1 | A447PA1040GCB08IMF | 49.3 | 3820 | Alfanar cables.pdf | 33 | 150 sm 0.2060 0.2494 196 158 206 49.3 3820 A447PA1040GCB08IMF
alfanar-1357 | Needs review | Conductor may be aluminium: Weight of 4,615 kg/km is too light for copper conductors (about 6,579 kg/km) but fits aluminium (about 1,998 kg/km); the conductor may be aluminium. | alfanar | 4-core 185 mm² | Cu/PVC/SWA | 0.6/1 kV | IEC 60502-1 | A448PA1040GCB08IMS | 54.5 | 4615 | Alfanar cables.pdf | 33 | 185 sm 0.1640 0.1994 222 181 237 54.5 4615 A448PA1040GCB08IMS
alfanar-1358 | Needs review | Conductor may be aluminium: Weight of 5,770 kg/km is too light for copper conductors (about 8,534 kg/km) but fits aluminium (about 2,592 kg/km); the conductor may be aluminium. | alfanar | 4-core 240 mm² | Cu/PVC/SWA | 0.6/1 kV | IEC 60502-1 | A449PA1040GCB08IMS | 61 | 5770 | Alfanar cables.pdf | 33 | 240 sm 0.1250 0.1533 257 212 281 61.0 5770 A449PA1040GCB08IMS
alfanar-1359 | Needs review | Conductor may be aluminium: Weight of 6,905 kg/km is too light for copper conductors (about 10,668 kg/km) but fits aluminium (about 3,240 kg/km); the conductor may be aluminium. | alfanar | 4-core 300 mm² | Cu/PVC/SWA | 0.6/1 kV | IEC 60502-1 | A450PA1040GCB08IMS | 67.1 | 6905 | Alfanar cables.pdf | 33 | 300 sm 0.1000 0.1240 290 242 323 67.1 6905 A450PA1040GCB08IMS
alfanar-1360 | Needs review | Conductor may be aluminium: Weight of 8,695 kg/km is too light for copper conductors (about 14,224 kg/km) but fits aluminium (about 4,320 kg/km); the conductor may be aluminium. | alfanar | 4-core 400 mm² | Cu/PVC/SWA | 0.6/1 kV | IEC 60502-1 | A451PA1040GCB08IMS | 76.1 | 8695 | Alfanar cables.pdf | 33 | 400 sm 0.0778 0.0984 333 281 378 76.1 8695 A451PA1040GCB08IMS
alfanar-1361 | Needs review | Conductor may be aluminium: Weight of 11,430 kg/km is too light for copper conductors (about 17,780 kg/km) but fits aluminium (about 5,400 kg/km); the conductor may be aluminium. | alfanar | 4-core 500 mm² | Cu/PVC/SWA | 0.6/1 kV | IEC 60502-1 | A452PA1040GCB08IMS | 85 | 11430 | Alfanar cables.pdf | 33 | 500 sm 0.0605 0.0789 377 322 436 85.0 11430 A452PA1040GCB08IMS
alfanar-1289 | Needs review | Core count missing: The catalogue gives no core count, so the OD of 14.2 mm cannot be checked against the size. | alfanar | multi-core 10 mm² | Cu/PVC/STA | 0.6/1 kV | IEC 60502-1 | A314PA1010ACB51IMR | 14.2 | 270 | Alfanar cables.pdf | 29 | 10 3.0800 3.7007 50 50 42 46 48 49 60 14.2 270 A314PA1010ACB51IMR
alfanar-1290 | Needs review | Core count missing: The catalogue gives no core count, so the OD of 15.2 mm cannot be checked against the size. | alfanar | multi-core 16 mm² | Cu/PVC/STA | 0.6/1 kV | IEC 60502-1 | A315PA1010ACB51IMR | 15.2 | 315 | Alfanar cables.pdf | 29 | 16 1.9100 2.2949 63 63 52 58 61 63 77 15.2 315 A315PA1010ACB51IMR
alfanar-1291 | Needs review | Core count missing: The catalogue gives no core count, so the OD of 16.8 mm cannot be checked against the size. | alfanar | multi-core 25 mm² | Cu/PVC/STA | 0.6/1 kV | IEC 60502-1 | A316PA1010ACB51IMR | 16.8 | 390 | Alfanar cables.pdf | 29 | 25 1.2000 1.4419 81 81 68 74 81 83 101 16.8 390 A316PA1010ACB51IMR
alfanar-1292 | Needs review | Core count missing: The catalogue gives no core count, so the OD of 18.0 mm cannot be checked against the size. | alfanar | multi-core 35 mm² | Cu/PVC/STA | 0.6/1 kV | IEC 60502-1 | A317PA1010ACB51IMR | 18 | 455 | Alfanar cables.pdf | 29 | 35 0.8680 1.0431 96 96 81 88 99 101 122 18.0 455 A317PA1010ACB51IMR
alfanar-1293 | Needs review | Core count missing: The catalogue gives no core count, so the OD of 19.6 mm cannot be checked against the size. | alfanar | multi-core 50 mm² | Cu/PVC/STA | 0.6/1 kV | IEC 60502-1 | A318PA1010ACB51IMR | 19.6 | 540 | Alfanar cables.pdf | 29 | 50 0.6410 0.7704 113 113 96 104 119 121 146 19.6 540 A318PA1010ACB51IMR
alfanar-1294 | Needs review | Core count missing: The catalogue gives no core count, so the OD of 21.4 mm cannot be checked against the size. | alfanar | multi-core 70 mm² | Cu/PVC/STA | 0.6/1 kV | IEC 60502-1 | A319PA1010ACB51IMR | 21.4 | 650 | Alfanar cables.pdf | 29 | 70 0.4430 0.5327 138 138 118 126 149 151 181 21.4 650 A319PA1010ACB51IMR
alfanar-1295 | Needs review | Core count missing: The catalogue gives no core count, so the OD of 23.4 mm cannot be checked against the size. | alfanar | multi-core 95 mm² | Cu/PVC/STA | 0.6/1 kV | IEC 60502-1 | A345PA1010ACB51IMR | 23.4 | 790 | Alfanar cables.pdf | 29 | 95 0.3200 0.3851 164 163 141 150 181 184 217 23.4 790 A345PA1010ACB51IMR
alfanar-1296 | Needs review | Core count missing: The catalogue gives no core count, so the OD of 24.9 mm cannot be checked against the size. | alfanar | multi-core 120 mm² | Cu/PVC/STA | 0.6/1 kV | IEC 60502-1 | A346PA1010ACB51IMR | 24.9 | 910 | Alfanar cables.pdf | 29 | 120 0.2530 0.3048 185 184 161 169 209 211 247 24.9 910 A346PA1010ACB51IMR
alfanar-1297 | Needs review | Core count missing: The catalogue gives no core count, so the OD of 26.8 mm cannot be checked against the size. | alfanar | multi-core 150 mm² | Cu/PVC/STA | 0.6/1 kV | IEC 60502-1 | A347PA1010ACB51IMR | 26.8 | 1060 | Alfanar cables.pdf | 29 | 150 0.2060 0.2486 207 205 181 188 238 238 277 26.8 1060 A347PA1010ACB51IMR
alfanar-1298 | Needs review | Core count missing: The catalogue gives no core count, so the OD of 29.1 mm cannot be checked against the size. | alfanar | multi-core 185 mm² | Cu/PVC/STA | 0.6/1 kV | IEC 60502-1 | A348PA1010ACB51IMR | 29.1 | 1255 | Alfanar cables.pdf | 29 | 185 0.1640 0.1984 233 230 205 210 273 272 312 29.1 1255 A348PA1010ACB51IMR
alfanar-1299 | Needs review | Core count missing: The catalogue gives no core count, so the OD of 32.0 mm cannot be checked against the size. | alfanar | multi-core 240 mm² | Cu/PVC/STA | 0.6/1 kV | IEC 60502-1 | A349PA1010ACB51IMR | 32 | 1535 | Alfanar cables.pdf | 29 | 240 0.1250 0.1521 267 262 237 239 321 316 357 32.0 1535 A349PA1010ACB51IMR
alfanar-1300 | Needs review | Core count missing: The catalogue gives no core count, so the OD of 35.8 mm cannot be checked against the size. | alfanar | multi-core 300 mm² | Cu/PVC/STA | 0.6/1 kV | IEC 60502-1 | A350PA1010ACB51IMR | 35.8 | 1920 | Alfanar cables.pdf | 29 | 300 0.1000 0.1225 296 288 265 258 367 353 390 35.8 1920 A350PA1010ACB51IMR
alfanar-1301 | Needs review | Core count missing: The catalogue gives no core count, so the OD of 39.4 mm cannot be checked against the size. | alfanar | multi-core 400 mm² | Cu/PVC/STA | 0.6/1 kV | IEC 60502-1 | A351PA1010ACB51IMR | 39.4 | 2355 | Alfanar cables.pdf | 29 | 400 0.0778 0.0966 330 320 299 283 420 397 432 39.4 2355 A351PA1010ACB51IMR
alfanar-1302 | Needs review | Core count missing: The catalogue gives no core count, so the OD of 43.4 mm cannot be checked against the size. | alfanar | multi-core 500 mm² | Cu/PVC/STA | 0.6/1 kV | IEC 60502-1 | A352PA1010ACB51IMF | 43.4 | 2870 | Alfanar cables.pdf | 29 | 500 0.0605 0.0768 367 353 335 309 479 444 478 43.4 2870 A352PA1010ACB51IMF
alfanar-1303 | Needs review | Core count missing: The catalogue gives no core count, so the OD of 47.4 mm cannot be checked against the size. | alfanar | multi-core 630 mm² | Cu/PVC/STA | 0.6/1 kV | IEC 60502-1 | A353PA1010ACB51IMF | 47.4 | 3470 | Alfanar cables.pdf | 29 | 630 0.0469 0.0617 403 385 372 334 541 490 523 47.4 3470 A353PA1010ACB51IMF
alfanar-1304 | Needs review | Core count missing: The catalogue gives no core count, so the OD of 52.8 mm cannot be checked against the size. | alfanar | multi-core 800 mm² | Cu/PVC/STA | 0.6/1 kV | IEC 60502-1 | A354PA1010ACB51IMF | 52.8 | 4390 | Alfanar cables.pdf | 29 | 800 0.0367 0.0506 426 408 397 353 589 525 569 52.8 4390 A354PA1010ACB51IMF
alfanar-1305 | Needs review | Core count missing: The catalogue gives no core count, so the OD of 61.5 mm cannot be checked against the size. | alfanar | multi-core 1,000 mm² | Cu/PVC/STA | 0.6/1 kV | IEC 60502-1 | A255PA1010ACB51IMF | 61.5 | 5455 | Alfanar cables.pdf | 29 | 1000 0.0291 0.0431 458 438 432 383 660 581 637 61.5 5455 A255PA1010ACB51IMF
bahra-158 | Needs review | Conductor may be aluminium: Weight of 905 kg/km is too light for copper conductors (about 1,245 kg/km) but fits aluminium (about 378 kg/km); the conductor may be aluminium. | Bahra Electric | 4-core 35 mm² | Cu/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | 14210302 | 27.8 | 905 | Bahra electric cables.pdf | 47 | 14210302 35sm 7 1.2 1.8 27.8 905 500/1000
bahra-216 | Needs review | Weight not plausible: Weight of 87.5 kg/km is less than the conductors alone (about 540 kg/km), so it is not used. | Bahra Electric | 4-core 50 mm² | Al/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | 14710303 | 25.7 | 87.5 | Bahra electric cables.pdf | 71 | 14710303 50smc 7 1.0 1.9 25.7 87.5 1000
bahra-159 | Needs review | Conductor may be aluminium: Weight of 1,063 kg/km is too light for copper conductors (about 1,778 kg/km) but fits aluminium (about 540 kg/km); the conductor may be aluminium. | Bahra Electric | 4-core 50 mm² | Cu/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | 14210303 | 27.9 | 1063 | Bahra electric cables.pdf | 47 | 14210303 50sm 7 1.4 1.9 27.9 1063 1000
bahra-160 | Needs review | Conductor may be aluminium: Weight of 1,380 kg/km is too light for copper conductors (about 2,489 kg/km) but fits aluminium (about 756 kg/km); the conductor may be aluminium. | Bahra Electric | 4-core 70 mm² | Cu/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | 14210304 | 31.4 | 1380 | Bahra electric cables.pdf | 47 | 14210304 70sm 19 1.4 2.0 31.4 1380 1000
bahra-161 | Needs review | Conductor may be aluminium: Weight of 1,869 kg/km is too light for copper conductors (about 3,378 kg/km) but fits aluminium (about 1,026 kg/km); the conductor may be aluminium. | Bahra Electric | 4-core 95 mm² | Cu/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | 14210305 | 36.4 | 1869 | Bahra electric cables.pdf | 47 | 14210305 95sm 19 1.6 2.2 36.4 1869 1000
bahra-162 | Needs review | Conductor may be aluminium: Weight of 2,275 kg/km is too light for copper conductors (about 4,267 kg/km) but fits aluminium (about 1,296 kg/km); the conductor may be aluminium. | Bahra Electric | 4-core 120 mm² | Cu/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | 14210306 | 39.6 | 2275 | Bahra electric cables.pdf | 47 | 14210306 120sm 19 1.6 2.3 39.6 2275 1000
bahra-163 | Needs review | Conductor may be aluminium: Weight of 2,745 kg/km is too light for copper conductors (about 5,334 kg/km) but fits aluminium (about 1,620 kg/km); the conductor may be aluminium. | Bahra Electric | 4-core 150 mm² | Cu/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | 14210307 | 43.9 | 2745 | Bahra electric cables.pdf | 47 | 14210307 150sm 19 1.8 2.5 43.9 2745 1000
bahra-236 | Needs review | OD out of size order: OD of 43.9 mm is larger than 40.6 mm for the larger 185 mm² size in the same product range. | Bahra Electric | 4-core 150 mm² | Cu/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | 14010317 | 43.9 | 6391 | Bahra electric cables.pdf | 43 | 14010317 150sm 37 1.8 2.5 43.9 6391 250
bahra-237 | Needs review | OD out of size order: OD of 40.6 mm is smaller than 43.9 mm for the smaller 150 mm² size in the same product range. | Bahra Electric | 4-core 185 mm² | Cu/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | 14010318 | 40.6 | 7843 | Bahra electric cables.pdf | 43 | 14010318 185sm 37 2.0 2.6 40.6 7843 250
bahra-164 | Needs review | Conductor may be aluminium: Weight of 3,404 kg/km is too light for copper conductors (about 6,579 kg/km) but fits aluminium (about 1,998 kg/km); the conductor may be aluminium. | Bahra Electric | 4-core 185 mm² | Cu/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | 14210308 | 48.8 | 3404 | Bahra electric cables.pdf | 47 | 14210308 185sm 37 2.0 2.7 48.8 3404 500
bahra-165 | Needs review | Conductor may be aluminium: Weight of 4,356 kg/km is too light for copper conductors (about 8,534 kg/km) but fits aluminium (about 2,592 kg/km); the conductor may be aluminium. | Bahra Electric | 4-core 240 mm² | Cu/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | 14210309 | 55.1 | 4356 | Bahra electric cables.pdf | 47 | 14210309 240sm 37 2.2 2.9 55.1 4356 500
bahra-166 | Needs review | Conductor may be aluminium: Weight of 4,209 kg/km is too light for copper conductors (about 10,668 kg/km) but fits aluminium (about 3,240 kg/km); the conductor may be aluminium. | Bahra Electric | 4-core 300 mm² | Cu/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | 14210310 | 62.3 | 4209 | Bahra electric cables.pdf | 47 | 14210310 300sm 37 2.4 3.1 62.3 4209 500
bahra-167 | Needs review | Conductor may be aluminium: Weight of 6,797 kg/km is too light for copper conductors (about 14,224 kg/km) but fits aluminium (about 4,320 kg/km); the conductor may be aluminium. | Bahra Electric | 4-core 400 mm² | Cu/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | 14210311 | 68.8 | 6797 | Bahra electric cables.pdf | 47 | 14210311 400sm 61 2.6 3.4 68.8 6797 500
bahra-168 | Needs review | Conductor may be aluminium: Weight of 8,574 kg/km is too light for copper conductors (about 17,780 kg/km) but fits aluminium (about 5,400 kg/km); the conductor may be aluminium. | Bahra Electric | 4-core 500 mm² | Cu/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | 14210312 | 76.2 | 8574 | Bahra electric cables.pdf | 47 | 14210312 500sm 61 2.8 3.6 76.2 8574 300
jeddah-2057 | Excluded | Impossible OD: OD of 713.0 mm is far too large for a 1-core 6 mm² cable (typically 3.5–16.0 mm); a decimal point was probably lost. | Jeddah Cable Company | 1-core 6 mm² | Cu/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 20 | 713 | 100 | Jeddah cables.pdf | 20 | 6 0.7 14 713 100 3.0810 4 7 57 73 66 59
jeddah-2060 | Excluded | Impossible OD: OD of 1.0 mm is smaller than the conductors of a 1-core 25 mm² cable (typically 7.9–24.8 mm). Weight not plausible: Weight of 310 kg/km is more than a solid copper rod of this OD, so it is not used. | Jeddah Cable Company | 1-core 25 mm² | Cu/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 20 | 1 | 310 | Jeddah cables.pdf | 20 | 25 0.9 1.4 1 310 0.7270 163 154 ¦ 120 159 152 ¦ 135
jeddah-2076 | Excluded | Impossible OD: OD of 113.0 mm is far too large for a 1-core 25 mm² cable (typically 7.9–24.8 mm); a decimal point was probably lost. | Jeddah Cable Company | 1-core 25 mm² | Al/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 21 | 113 | 165 | Jeddah cables.pdf | 21 | 25 09 14 113 ¦ 165 1.2000 123 ¦ 120 1 129 ¦ 123 ¦ 105
jeddah-2078 | Excluded | Impossible OD: OD of 160.0 mm is far too large for a 1-core 70 mm² cable (typically 14.2–34.0 mm); a decimal point was probably lost. | Jeddah Cable Company | 1-core 70 mm² | Al/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 21 | 160 | 340 | Jeddah cables.pdf | 21 | 70 1A 14 160 ¦ 340 ¦ 0.4430 217 ¦ 205 ¦ 165 ¦ 246 ¦ 240 ¦ 199
jeddah-2064 | Excluded | Impossible OD: OD of 167.0 mm is far too large for a 1-core 95 mm² cable (typically 16.5–39.6 mm); a decimal point was probably lost. | Jeddah Cable Company | 1-core 95 mm² | Cu/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 20 | 167 | 980 | Jeddah cables.pdf | 20 | 95 14 15 167 ¦ 980 0.1980 336 319 ¦ 262 386 374 ¦ 322
jeddah-2065 | Excluded | Impossible OD: OD of 184.0 mm is far too large for a 1-core 120 mm² cable (typically 17.3–34.6 mm); a decimal point was probably lost. | Jeddah Cable Company | 1-core 120 mm² | Cu/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 20 | 184 | 1210 | Jeddah cables.pdf | 20 | 120 12 15 184 ¦ 1210 ¦ 0.1530 388 371 296 450 ¦ 439 ¦ 380
jeddah-2066 | Excluded | Impossible OD: OD of 205.0 mm is far too large for a 1-core 150 mm² cable (typically 19.3–38.7 mm); a decimal point was probably lost. | Jeddah Cable Company | 1-core 150 mm² | Cu/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 20 | 205 | 1500 | Jeddah cables.pdf | 20 | 150 14 1.6 205 ¦ 1500 ¦ 0.1240 428 405 ¦ 336 509 497 ¦ 433
jeddah-2081 | Excluded | Impossible OD: OD of 205.0 mm is far too large for a 1-core 150 mm² cable (typically 19.3–38.7 mm); a decimal point was probably lost. | Jeddah Cable Company | 1-core 150 mm² | Al/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 21 | 205 | 570 | Jeddah cables.pdf | 21 | 150 14 1.6 205 ¦ 570 ¦ 0.2060 336 ¦ 319 ¦ 257 ¦ 415 ¦ 404 ¦ 333
jeddah-2067 | Excluded | Impossible OD: OD of 225.0 mm is far too large for a 1-core 185 mm² cable (typically 21.5–43.0 mm); a decimal point was probably lost. | Jeddah Cable Company | 1-core 185 mm² | Cu/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 20 | 225 | 1840 | Jeddah cables.pdf | 20 | 185 1.6 16 225 ¦ 1840 ¦ 0.0991 490 462 ¦ 382 591 579 ¦ 491
jeddah-2083 | Excluded | Impossible OD: OD of 270.0 mm is far too large for a 1-core 240 mm² cable (typically 24.5–48.9 mm); a decimal point was probably lost. | Jeddah Cable Company | 1-core 240 mm² | Al/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 21 | 270 | 1050 | Jeddah cables.pdf | 21 | 240 17 1.7 270 ¦ 1050 ¦ 0.1250 445 ¦ 422 ¦ 342 ¦ 573 ¦ 556 ¦ 445
jeddah-2068 | Excluded | Impossible OD: OD of 2,400.0 mm is far too large for a 1-core 240 mm² cable (typically 24.5–48.9 mm); a decimal point was probably lost. Weight not plausible: Weight of 0.08 kg/km is less than the conductors alone (about 2,134 kg/km), so it is not used. | Jeddah Cable Company | 1-core 240 mm² | Cu/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 20 | 2400 | 0.0754 | Jeddah cables.pdf | 20 | 240 17 sd 25.4 ¦ 2400 ¦ 0.0754 564 ¦ 530 ¦ 439 725 714 ¦ 597
jeddah-2069 | Excluded | Impossible OD: OD of 278.0 mm is far too large for a 1-core 300 mm² cable (typically 27.4–54.7 mm); a decimal point was probably lost. | Jeddah Cable Company | 1-core 300 mm² | Cu/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 20 | 278 | 2995 | Jeddah cables.pdf | 20 | 300 1.8 18 278 ¦ 2995 ¦ 0.0601 638 593 ¦ 496 918 842 ¦ 690
jeddah-2084 | Excluded | Impossible OD: OD of 278.0 mm is far too large for a 1-core 300 mm² cable (typically 27.4–54.7 mm); a decimal point was probably lost. | Jeddah Cable Company | 1-core 300 mm² | Al/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 21 | 278 | 1300 | Jeddah cables.pdf | 21 | 300 18 18 278 ¦ 1300 ¦ 0.1000 507 ¦ 473 ¦ 388 ¦ 644 ¦ 632 ¦ 515
jeddah-2086 | Excluded | Impossible OD: OD of 2,000.0 mm is far too large for a 1-core 500 mm² cable (typically 34.6–58.0 mm); a decimal point was probably lost. Weight not plausible: Weight of 0.06 kg/km is less than the conductors alone (about 1,350 kg/km), so it is not used. | Jeddah Cable Company | 1-core 500 mm² | Al/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 21 | 2000 | 0.0605 | Jeddah cables.pdf | 21 | 500 PIP) 2.0 36.2 ¦ 2000 ¦ 0.0605 661 eis ¦ 507 ¦ 901 878 ¦ 702
jeddah-2073 | Excluded | Impossible OD: OD of 468.0 mm is far too large for a 1-core 800 mm² cable (typically 43.7–73.4 mm); a decimal point was probably lost. | Jeddah Cable Company | 1-core 800 mm² | Cu/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 20 | 468 | 8260 | Jeddah cables.pdf | 20 | 800 2.6 2.3 468 ¦ 8260 ¦ 0.0221 i060 ¦ 935 ¦ 798 ¦ 1463 ¦ 1439 ¦ 1217
jeddah-2088 | Excluded | Impossible OD: OD of 468.0 mm is far too large for a 1-core 800 mm² cable (typically 43.7–73.4 mm); a decimal point was probably lost. | Jeddah Cable Company | 1-core 800 mm² | Al/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 21 | 468 | 3150 | Jeddah cables.pdf | 21 | 800 26 23 468 ¦ 3150 ¦ 0.0367 a55 ¦ 764 ¦ 650 ¦ 1193 ¦ 1170 ¦ 948
jeddah-2074 | Excluded | Impossible OD: OD of 511.0 mm is far too large for a 1-core 1,000 mm² cable (typically 48.9–82.1 mm); a decimal point was probably lost. | Jeddah Cable Company | 1-core 1,000 mm² | Cu/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 20 | 511 | 9745 | Jeddah cables.pdf | 20 | 1000 2.8 24 511 ¦ 9745 ¦ 0.0176 1174 ¦ 1016 ¦ see ¦ 1615 ¦ 1591 ¦ 1346
jeddah-2089 | Excluded | Impossible OD: OD of 518.0 mm is far too large for a 1-core 1,000 mm² cable (typically 48.9–82.1 mm); a decimal point was probably lost. | Jeddah Cable Company | 1-core 1,000 mm² | Al/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 21 | 518 | 3870 | Jeddah cables.pdf | 21 | 1000 2.8 24 518 ¦ 3870 ¦ 0.0291 o46 ¦ a32 ¦ 707 ¦ 1310 ¦ 1287 ¦ 1076
oman-100477 | Excluded | Impossible OD: OD of 2,255.0 mm is far too large for a 4-core 500 mm² cable (typically 70.1–106.0 mm); a decimal point was probably lost. Weight not plausible: Weight of 250 kg/km is less than the conductors alone (about 5,400 kg/km), so it is not used. | Oman Cables | 4-core 500 mm² | Al/XLPE/SWA | 0.6/1 kV | IEC 60502-1 | page 55 | 2255 | 250 | Oman Cables.pdf | 55 | Physical Dimensions table
oman-100163 | Excluded | Impossible OD: OD of 2,200.0 mm is far too large for a 4-core 630 mm² cable (typically 78.7–119.0 mm); a decimal point was probably lost. Weight not plausible: Weight of 250 kg/km is less than the conductors alone (about 6,804 kg/km), so it is not used. | Oman Cables | 4-core 630 mm² | Al/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 29 | 2200 | 250 | Oman Cables.pdf | 29 | Physical Dimensions table
oman-100481 | Excluded | Impossible OD: OD of 2,800.0 mm is far too large for a 4-core 630 mm² cable (typically 78.7–119.0 mm); a decimal point was probably lost. Weight not plausible: Weight of 250 kg/km is less than the conductors alone (about 6,804 kg/km), so it is not used. | Oman Cables | 4-core 630 mm² | Al/XLPE/SWA | 0.6/1 kV | IEC 60502-1 | page 55 | 2800 | 250 | Oman Cables.pdf | 55 | Physical Dimensions table
oman-100323 | Excluded | Impossible OD: OD of 265.0 mm is far too large for a 5-core 1.5 mm² cable (typically 3.9–17.9 mm); a decimal point was probably lost. | Oman Cables | 5-core 1.5 mm² | Cu/XLPE/SWA | 0.6/1 kV | IEC 60502-1 | page 49 | 265 | 1000 | Oman Cables.pdf | 49 | Physical Dimensions table
oman-100486 | Excluded | Impossible OD: OD of 275.0 mm is far too large for a 5-core 1.5 mm² cable (typically 3.9–17.9 mm); a decimal point was probably lost. | Oman Cables | 5-core 1.5 mm² | Cu/XLPE/SWA | 0.6/1 kV | BS 5467 | page 61 | 275 | 1000 | Oman Cables.pdf | 61 | Physical Dimensions table
oman-100571 | Excluded | Impossible OD: OD of 305.0 mm is far too large for a 5-core 1.5 mm² cable (typically 3.9–17.9 mm); a decimal point was probably lost. | Oman Cables | 5-core 1.5 mm² | Cu/PVC/SWA | 0.6/1 kV | IEC 60502-1 | page 67 | 305 | 1000 | Oman Cables.pdf | 67 | Physical Dimensions table
oman-100328 | Excluded | Impossible OD: OD of 310.0 mm is far too large for a 5-core 2.5 mm² cable (typically 5.0–23.1 mm); a decimal point was probably lost. | Oman Cables | 5-core 2.5 mm² | Cu/XLPE/SWA | 0.6/1 kV | IEC 60502-1 | page 49 | 310 | 1000 | Oman Cables.pdf | 49 | Physical Dimensions table
oman-100491 | Excluded | Impossible OD: OD of 340.0 mm is far too large for a 5-core 2.5 mm² cable (typically 5.0–23.1 mm); a decimal point was probably lost. | Oman Cables | 5-core 2.5 mm² | Cu/XLPE/SWA | 0.6/1 kV | BS 5467 | page 61 | 340 | 1000 | Oman Cables.pdf | 61 | Physical Dimensions table
oman-100576 | Excluded | Impossible OD: OD of 345.0 mm is far too large for a 5-core 2.5 mm² cable (typically 5.0–23.1 mm); a decimal point was probably lost. | Oman Cables | 5-core 2.5 mm² | Cu/PVC/SWA | 0.6/1 kV | IEC 60502-1 | page 67 | 345 | 1000 | Oman Cables.pdf | 67 | Physical Dimensions table
oman-100333 | Excluded | Impossible OD: OD of 370.0 mm is far too large for a 5-core 4 mm² cable (typically 7.1–22.2 mm); a decimal point was probably lost. | Oman Cables | 5-core 4 mm² | Cu/XLPE/SWA | 0.6/1 kV | IEC 60502-1 | page 49 | 370 | 1000 | Oman Cables.pdf | 49 | Physical Dimensions table
oman-100496 | Excluded | Impossible OD: OD of 415.0 mm is far too large for a 5-core 4 mm² cable (typically 7.1–22.2 mm); a decimal point was probably lost. | Oman Cables | 5-core 4 mm² | Cu/XLPE/SWA | 0.6/1 kV | BS 5467 | page 61 | 415 | 1000 | Oman Cables.pdf | 61 | Physical Dimensions table
oman-100581 | Excluded | Impossible OD: OD of 445.0 mm is far too large for a 5-core 4 mm² cable (typically 7.1–22.2 mm); a decimal point was probably lost. | Oman Cables | 5-core 4 mm² | Cu/PVC/SWA | 0.6/1 kV | IEC 60502-1 | page 67 | 445 | 1000 | Oman Cables.pdf | 67 | Physical Dimensions table
oman-100338 | Excluded | Impossible OD: OD of 445.0 mm is far too large for a 5-core 6 mm² cable (typically 8.7–27.2 mm); a decimal point was probably lost. | Oman Cables | 5-core 6 mm² | Cu/XLPE/SWA | 0.6/1 kV | IEC 60502-1 | page 49 | 445 | 1000 | Oman Cables.pdf | 49 | Physical Dimensions table
oman-100501 | Excluded | Impossible OD: OD of 505.0 mm is far too large for a 5-core 6 mm² cable (typically 8.7–27.2 mm); a decimal point was probably lost. | Oman Cables | 5-core 6 mm² | Cu/XLPE/SWA | 0.6/1 kV | BS 5467 | page 61 | 505 | 1000 | Oman Cables.pdf | 61 | Physical Dimensions table
oman-100586 | Excluded | Impossible OD: OD of 595.0 mm is far too large for a 5-core 6 mm² cable (typically 8.7–27.2 mm); a decimal point was probably lost. | Oman Cables | 5-core 6 mm² | Cu/PVC/SWA | 0.6/1 kV | IEC 60502-1 | page 67 | 595 | 1000 | Oman Cables.pdf | 67 | Physical Dimensions table
oman-100536 | Excluded | Impossible OD: OD of 1,145.0 mm is far too large for a 5-core 95 mm² cable (typically 33.7–56.6 mm); a decimal point was probably lost. Weight not plausible: Weight of 500 kg/km is less than the conductors alone (about 4,223 kg/km), so it is not used. | Oman Cables | 5-core 95 mm² | Cu/XLPE/SWA | 0.6/1 kV | BS 5467 | page 61 | 1145 | 500 | Oman Cables.pdf | 61 | Physical Dimensions table
oman-100541 | Excluded | Impossible OD: OD of 1,395.0 mm is far too large for a 5-core 120 mm² cable (typically 37.9–63.6 mm); a decimal point was probably lost. Weight not plausible: Weight of 500 kg/km is less than the conductors alone (about 5,334 kg/km), so it is not used. | Oman Cables | 5-core 120 mm² | Cu/XLPE/SWA | 0.6/1 kV | BS 5467 | page 61 | 1395 | 500 | Oman Cables.pdf | 61 | Physical Dimensions table
oman-100546 | Excluded | Impossible OD: OD of 1,755.0 mm is far too large for a 5-core 150 mm² cable (typically 42.3–71.1 mm); a decimal point was probably lost. Weight not plausible: Weight of 500 kg/km is less than the conductors alone (about 6,668 kg/km), so it is not used. | Oman Cables | 5-core 150 mm² | Cu/XLPE/SWA | 0.6/1 kV | BS 5467 | page 61 | 1755 | 500 | Oman Cables.pdf | 61 | Physical Dimensions table
oman-100551 | Excluded | Impossible OD: OD of 2,150.0 mm is far too large for a 5-core 185 mm² cable (typically 47.0–78.9 mm); a decimal point was probably lost. Weight not plausible: Weight of 500 kg/km is less than the conductors alone (about 8,223 kg/km), so it is not used. | Oman Cables | 5-core 185 mm² | Cu/XLPE/SWA | 0.6/1 kV | BS 5467 | page 61 | 2150 | 500 | Oman Cables.pdf | 61 | Physical Dimensions table
oman-100556 | Excluded | Impossible OD: OD of 2,725.0 mm is far too large for a 5-core 240 mm² cable (typically 54.3–82.1 mm); a decimal point was probably lost. Weight not plausible: Weight of 500 kg/km is less than the conductors alone (about 10,668 kg/km), so it is not used. | Oman Cables | 5-core 240 mm² | Cu/XLPE/SWA | 0.6/1 kV | BS 5467 | page 61 | 2725 | 500 | Oman Cables.pdf | 61 | Physical Dimensions table
oman-100561 | Excluded | Impossible OD: OD of 3,335.0 mm is far too large for a 5-core 300 mm² cable (typically 60.7–91.8 mm); a decimal point was probably lost. Weight not plausible: Weight of 500 kg/km is less than the conductors alone (about 13,335 kg/km), so it is not used. | Oman Cables | 5-core 300 mm² | Cu/XLPE/SWA | 0.6/1 kV | BS 5467 | page 61 | 3335 | 500 | Oman Cables.pdf | 61 | Physical Dimensions table
oman-100566 | Excluded | Impossible OD: OD of 4,275.0 mm is far too large for a 5-core 400 mm² cable (typically 70.1–106.0 mm); a decimal point was probably lost. Weight not plausible: Weight of 500 kg/km is less than the conductors alone (about 17,780 kg/km), so it is not used. | Oman Cables | 5-core 400 mm² | Cu/XLPE/SWA | 0.6/1 kV | BS 5467 | page 61 | 4275 | 500 | Oman Cables.pdf | 61 | Physical Dimensions table
oman-100159 | Excluded | Impossible OD: OD of 1,705.0 mm is far too large for a 5-core 500 mm² cable (typically 78.4–118.5 mm); a decimal point was probably lost. Weight not plausible: Weight of 250 kg/km is less than the conductors alone (about 6,750 kg/km), so it is not used. | Oman Cables | 5-core 500 mm² | Al/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 29 | 1705 | 250 | Oman Cables.pdf | 29 | Physical Dimensions table
oman-100726 | Excluded | Impossible OD: OD of 2,565.0 mm is far too large for a 5-core 500 mm² cable (typically 78.4–118.5 mm); a decimal point was probably lost. Weight not plausible: Weight of 250 kg/km is less than the conductors alone (about 6,750 kg/km), so it is not used. | Oman Cables | 5-core 500 mm² | Al/PVC/SWA | 0.6/1 kV | IEC 60502-1 | page 73 | 2565 | 250 | Oman Cables.pdf | 73 | Physical Dimensions table
oman-100253 | Excluded | Impossible OD: OD of 4,955.0 mm is far too large for a 5-core 500 mm² cable (typically 78.4–118.5 mm); a decimal point was probably lost. Weight not plausible: Weight of 500 kg/km is less than the conductors alone (about 22,225 kg/km), so it is not used. | Oman Cables | 5-core 500 mm² | Cu/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 35 | 4955 | 500 | Oman Cables.pdf | 35 | Physical Dimensions table
oman-100408 | Excluded | Impossible OD: OD of 5,285.0 mm is far too large for a 5-core 500 mm² cable (typically 78.4–118.5 mm); a decimal point was probably lost. Weight not plausible: Weight of 250 kg/km is less than the conductors alone (about 22,225 kg/km), so it is not used. | Oman Cables | 5-core 500 mm² | Cu/XLPE/SWA | 0.6/1 kV | IEC 60502-1 | page 49 | 5285 | 250 | Oman Cables.pdf | 49 | Physical Dimensions table
oman-100656 | Excluded | Impossible OD: OD of 5,555.0 mm is far too large for a 5-core 500 mm² cable (typically 78.4–118.5 mm); a decimal point was probably lost. Weight not plausible: Weight of 250 kg/km is less than the conductors alone (about 22,225 kg/km), so it is not used. | Oman Cables | 5-core 500 mm² | Cu/PVC/SWA | 0.6/1 kV | IEC 60502-1 | page 67 | 5555 | 250 | Oman Cables.pdf | 67 | Physical Dimensions table
oman-100094 | Excluded | Impossible OD: OD of 3,055.0 mm is far too large for a 5-core 630 mm² cable (typically 88.0–133.0 mm); a decimal point was probably lost. Weight not plausible: Weight of 500 kg/km is less than the conductors alone (about 28,004 kg/km), so it is not used. | Oman Cables | 5-core 630 mm² | Cu/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 23 | 3055 | 500 | Oman Cables.pdf | 23 | Physical Dimensions table
oman-100731 | Excluded | Impossible OD: OD of 3,145.0 mm is far too large for a 5-core 630 mm² cable (typically 88.0–133.0 mm); a decimal point was probably lost. Weight not plausible: Weight of 250 kg/km is less than the conductors alone (about 8,505 kg/km), so it is not used. | Oman Cables | 5-core 630 mm² | Al/PVC/SWA | 0.6/1 kV | IEC 60502-1 | page 73 | 3145 | 250 | Oman Cables.pdf | 73 | Physical Dimensions table
oman-100258 | Excluded | Impossible OD: OD of 6,320.0 mm is far too large for a 5-core 630 mm² cable (typically 88.0–133.0 mm); a decimal point was probably lost. Weight not plausible: Weight of 250 kg/km is less than the conductors alone (about 28,004 kg/km), so it is not used. | Oman Cables | 5-core 630 mm² | Cu/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 35 | 6320 | 250 | Oman Cables.pdf | 35 | Physical Dimensions table
oman-100413 | Excluded | Impossible OD: OD of 6,710.0 mm is far too large for a 5-core 630 mm² cable (typically 88.0–133.0 mm); a decimal point was probably lost. Weight not plausible: Weight of 250 kg/km is less than the conductors alone (about 28,004 kg/km), so it is not used. | Oman Cables | 5-core 630 mm² | Cu/XLPE/SWA | 0.6/1 kV | IEC 60502-1 | page 49 | 6710 | 250 | Oman Cables.pdf | 49 | Physical Dimensions table
oman-100661 | Excluded | Impossible OD: OD of 6,995.0 mm is far too large for a 5-core 630 mm² cable (typically 88.0–133.0 mm); a decimal point was probably lost. Weight not plausible: Weight of 250 kg/km is less than the conductors alone (about 28,004 kg/km), so it is not used. | Oman Cables | 5-core 630 mm² | Cu/PVC/SWA | 0.6/1 kV | IEC 60502-1 | page 67 | 6995 | 250 | Oman Cables.pdf | 67 | Physical Dimensions table
oman-100497 | Needs review | OD out of size order: OD of 15.0 mm is larger than 11.5 mm for the larger 10 mm² size in the same product range. | Oman Cables | 1-core 6 mm² | Cu/XLPE/SWA | 0.6/1 kV | BS 5467 | page 61 | 15 | 510 | Oman Cables.pdf | 61 | Physical Dimensions table
oman-100334 | Needs review | OD out of size order: OD of 16.0 mm is larger than 11.5 mm for the larger 10 mm² size in the same product range. | Oman Cables | 1-core 6 mm² | Cu/XLPE/SWA | 0.6/1 kV | IEC 60502-1 | page 49 | 16 | 510 | Oman Cables.pdf | 49 | Physical Dimensions table
oman-100582 | Needs review | OD out of size order: OD of 17.5 mm is larger than 12.0 mm for the larger 10 mm² size in the same product range. | Oman Cables | 1-core 6 mm² | Cu/PVC/SWA | 0.6/1 kV | IEC 60502-1 | page 67 | 17.5 | 685 | Oman Cables.pdf | 67 | Physical Dimensions table
oman-100339 | Needs review | OD out of size order: OD of 11.5 mm is smaller than 16.0 mm for the smaller 6 mm² size in the same product range. | Oman Cables | 1-core 10 mm² | Cu/XLPE/SWA | 0.6/1 kV | IEC 60502-1 | page 49 | 11.5 | 205 | Oman Cables.pdf | 49 | Physical Dimensions table
oman-100502 | Needs review | OD out of size order: OD of 11.5 mm is smaller than 15.0 mm for the smaller 6 mm² size in the same product range. | Oman Cables | 1-core 10 mm² | Cu/XLPE/SWA | 0.6/1 kV | BS 5467 | page 61 | 11.5 | 210 | Oman Cables.pdf | 61 | Physical Dimensions table
oman-100587 | Needs review | OD out of size order: OD of 12.0 mm is smaller than 17.5 mm for the smaller 6 mm² size in the same product range. | Oman Cables | 1-core 10 mm² | Cu/PVC/SWA | 0.6/1 kV | IEC 60502-1 | page 67 | 12 | 235 | Oman Cables.pdf | 67 | Physical Dimensions table
oman-100532 | Needs review | Weight not plausible: Weight of 3,920 kg/km is more than a solid copper rod of this OD, so it is not used. | Oman Cables | 1-core 95 mm² | Cu/XLPE/SWA | 0.6/1 kV | BS 5467 | page 61 | 20.5 | 3920 | Oman Cables.pdf | 61 | Physical Dimensions table
oman-100537 | Needs review | Weight not plausible: Weight of 4,760 kg/km is more than a solid copper rod of this OD, so it is not used. | Oman Cables | 1-core 120 mm² | Cu/XLPE/SWA | 0.6/1 kV | BS 5467 | page 61 | 22 | 4760 | Oman Cables.pdf | 61 | Physical Dimensions table
oman-100542 | Needs review | Weight not plausible: Weight of 6,140 kg/km is more than a solid copper rod of this OD, so it is not used. | Oman Cables | 1-core 150 mm² | Cu/XLPE/SWA | 0.6/1 kV | BS 5467 | page 61 | 25 | 6140 | Oman Cables.pdf | 61 | Physical Dimensions table
oman-100547 | Needs review | Weight not plausible: Weight of 7,370 kg/km is more than a solid copper rod of this OD, so it is not used. | Oman Cables | 1-core 185 mm² | Cu/XLPE/SWA | 0.6/1 kV | BS 5467 | page 61 | 27.5 | 7370 | Oman Cables.pdf | 61 | Physical Dimensions table
oman-100304 | Needs review | Weight not plausible: Weight of 1,000 kg/km equals the drum length; the columns were probably mixed up, so it is not used. | Oman Cables | 1-core 240 mm² | Al/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 41 | 26 | 1000 | Oman Cables.pdf | 41 | Physical Dimensions table
oman-100552 | Needs review | Weight not plausible: Weight of 9,260 kg/km is more than a solid copper rod of this OD, so it is not used. | Oman Cables | 1-core 240 mm² | Cu/XLPE/SWA | 0.6/1 kV | BS 5467 | page 61 | 30 | 9260 | Oman Cables.pdf | 61 | Physical Dimensions table
oman-100846 | Needs review | Conductor may be aluminium: Weight of 1,361 kg/km is too light for copper conductors (about 2,134 kg/km) but fits aluminium (about 648 kg/km); the conductor may be aluminium. | Oman Cables | 1-core 240 mm² | Cu/XLPE/AWA | 1.8/3 kV | IEC 60502-1 | page 107 | 30.5 | 1361 | Oman Cables.pdf | 107 | Physical Dimensions table
oman-100912 | Needs review | Conductor may be aluminium: Weight of 1,409 kg/km is too light for copper conductors (about 2,134 kg/km) but fits aluminium (about 648 kg/km); the conductor may be aluminium. | Oman Cables | 1-core 240 mm² | Cu/PVC/AWA | 1.8/3 kV | IEC 60502-1 | page 125 | 31 | 1409 | Oman Cables.pdf | 125 | Physical Dimensions table
oman-100557 | Needs review | Weight not plausible: Weight of 11,250 kg/km is more than a solid copper rod of this OD, so it is not used. | Oman Cables | 1-core 300 mm² | Cu/XLPE/SWA | 0.6/1 kV | BS 5467 | page 61 | 32.5 | 11250 | Oman Cables.pdf | 61 | Physical Dimensions table
oman-100848 | Needs review | Conductor may be aluminium: Weight of 1,660 kg/km is too light for copper conductors (about 2,667 kg/km) but fits aluminium (about 810 kg/km); the conductor may be aluminium. | Oman Cables | 1-core 300 mm² | Cu/XLPE/AWA | 1.8/3 kV | IEC 60502-1 | page 107 | 33 | 1660 | Oman Cables.pdf | 107 | Physical Dimensions table
oman-100914 | Needs review | Conductor may be aluminium: Weight of 1,766 kg/km is too light for copper conductors (about 2,667 kg/km) but fits aluminium (about 810 kg/km); the conductor may be aluminium. | Oman Cables | 1-core 300 mm² | Cu/PVC/AWA | 1.8/3 kV | IEC 60502-1 | page 125 | 34.5 | 1766 | Oman Cables.pdf | 125 | Physical Dimensions table
oman-100080 | Needs review | Conductor may be aluminium: Weight of 1,851 kg/km is too light for copper conductors (about 3,556 kg/km) but fits aluminium (about 1,080 kg/km); the conductor may be aluminium. | Oman Cables | 1-core 400 mm² | Cu/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 23 | 30.5 | 1851 | Oman Cables.pdf | 23 | Physical Dimensions table
oman-100562 | Needs review | Weight not plausible: Weight of 13,975 kg/km is more than a solid copper rod of this OD, so it is not used. | Oman Cables | 1-core 400 mm² | Cu/XLPE/SWA | 0.6/1 kV | BS 5467 | page 61 | 37 | 13975 | Oman Cables.pdf | 61 | Physical Dimensions table
oman-100850 | Needs review | Conductor may be aluminium: Weight of 2,117 kg/km is too light for copper conductors (about 3,556 kg/km) but fits aluminium (about 1,080 kg/km); the conductor may be aluminium. | Oman Cables | 1-core 400 mm² | Cu/XLPE/AWA | 1.8/3 kV | IEC 60502-1 | page 107 | 37 | 2117 | Oman Cables.pdf | 107 | Physical Dimensions table
oman-100916 | Needs review | Conductor may be aluminium: Weight of 2,212 kg/km is too light for copper conductors (about 3,556 kg/km) but fits aluminium (about 1,080 kg/km); the conductor may be aluminium. | Oman Cables | 1-core 400 mm² | Cu/PVC/AWA | 1.8/3 kV | IEC 60502-1 | page 125 | 38 | 2212 | Oman Cables.pdf | 125 | Physical Dimensions table
oman-100085 | Needs review | Conductor may be aluminium: Weight of 2,366 kg/km is too light for copper conductors (about 4,445 kg/km) but fits aluminium (about 1,350 kg/km); the conductor may be aluminium. | Oman Cables | 1-core 500 mm² | Cu/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 23 | 34.5 | 2366 | Oman Cables.pdf | 23 | Physical Dimensions table
oman-100249 | Needs review | Weight not plausible: Weight of 10,390 kg/km is more than a solid copper rod of this OD, so it is not used. | Oman Cables | 1-core 500 mm² | Cu/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 35 | 35.5 | 10390 | Oman Cables.pdf | 35 | Physical Dimensions table
oman-100404 | Needs review | Weight not plausible: Weight of 12,525 kg/km is more than a solid copper rod of this OD, so it is not used. | Oman Cables | 1-core 500 mm² | Cu/XLPE/SWA | 0.6/1 kV | IEC 60502-1 | page 49 | 40.5 | 12525 | Oman Cables.pdf | 49 | Physical Dimensions table
oman-100652 | Needs review | Weight not plausible: Weight of 13,555 kg/km is more than a solid copper rod of this OD, so it is not used. | Oman Cables | 1-core 500 mm² | Cu/PVC/SWA | 0.6/1 kV | IEC 60502-1 | page 67 | 42 | 13555 | Oman Cables.pdf | 67 | Physical Dimensions table
oman-100254 | Needs review | Weight not plausible: Weight of 13,225 kg/km is more than a solid copper rod of this OD, so it is not used. | Oman Cables | 1-core 630 mm² | Cu/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 35 | 39.5 | 13225 | Oman Cables.pdf | 35 | Physical Dimensions table
oman-100409 | Needs review | Weight not plausible: Weight of 15,770 kg/km is more than a solid copper rod of this OD, so it is not used. | Oman Cables | 1-core 630 mm² | Cu/XLPE/SWA | 0.6/1 kV | IEC 60502-1 | page 49 | 45 | 15770 | Oman Cables.pdf | 49 | Physical Dimensions table
oman-100657 | Needs review | Weight not plausible: Weight of 16,675 kg/km is more than a solid copper rod of this OD, so it is not used. | Oman Cables | 1-core 630 mm² | Cu/PVC/SWA | 0.6/1 kV | IEC 60502-1 | page 67 | 46 | 16675 | Oman Cables.pdf | 67 | Physical Dimensions table
oman-100061 | Needs review | Conductor may be aluminium: Weight of 1,502 kg/km is too light for copper conductors (about 2,667 kg/km) but fits aluminium (about 810 kg/km); the conductor may be aluminium. | Oman Cables | 2-core 150 mm² | Cu/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 23 | 31 | 1502 | Oman Cables.pdf | 23 | Physical Dimensions table
oman-100066 | Needs review | Conductor may be aluminium: Weight of 1,859 kg/km is too light for copper conductors (about 3,289 kg/km) but fits aluminium (about 999 kg/km); the conductor may be aluminium. | Oman Cables | 2-core 185 mm² | Cu/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 23 | 33.5 | 1859 | Oman Cables.pdf | 23 | Physical Dimensions table
oman-100071 | Needs review | Conductor may be aluminium: Weight of 2,431 kg/km is too light for copper conductors (about 4,267 kg/km) but fits aluminium (about 1,296 kg/km); the conductor may be aluminium. | Oman Cables | 2-core 240 mm² | Cu/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 23 | 40.5 | 2431 | Oman Cables.pdf | 23 | Physical Dimensions table
oman-100076 | Needs review | Conductor may be aluminium: Weight of 3,032 kg/km is too light for copper conductors (about 5,334 kg/km) but fits aluminium (about 1,620 kg/km); the conductor may be aluminium. | Oman Cables | 2-core 300 mm² | Cu/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 23 | 44.5 | 3032 | Oman Cables.pdf | 23 | Physical Dimensions table
oman-100081 | Needs review | Conductor may be aluminium: Weight of 3,874 kg/km is too light for copper conductors (about 7,112 kg/km) but fits aluminium (about 2,160 kg/km); the conductor may be aluminium. | Oman Cables | 2-core 400 mm² | Cu/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 23 | 49.5 | 3874 | Oman Cables.pdf | 23 | Physical Dimensions table
oman-100086 | Needs review | Conductor may be aluminium: Weight of 4,954 kg/km is too light for copper conductors (about 8,890 kg/km) but fits aluminium (about 2,700 kg/km); the conductor may be aluminium. | Oman Cables | 2-core 500 mm² | Cu/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 23 | 53.5 | 4954 | Oman Cables.pdf | 23 | Physical Dimensions table
oman-100475 | Needs review | Weight not plausible: Weight of 500 kg/km is less than the conductors alone (about 2,700 kg/km), so it is not used. | Oman Cables | 2-core 500 mm² | Al/XLPE/SWA | 0.6/1 kV | IEC 60502-1 | page 55 | 72 | 500 | Oman Cables.pdf | 55 | Physical Dimensions table
oman-100091 | Needs review | Conductor may be aluminium: Weight of 4,730 kg/km is too light for copper conductors (about 11,201 kg/km) but fits aluminium (about 3,402 kg/km); the conductor may be aluminium. | Oman Cables | 2-core 630 mm² | Cu/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 23 | 60 | 4730 | Oman Cables.pdf | 23 | Physical Dimensions table
oman-100161 | Needs review | Weight not plausible: Weight of 500 kg/km is less than the conductors alone (about 3,402 kg/km), so it is not used. | Oman Cables | 2-core 630 mm² | Al/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 29 | 69.5 | 500 | Oman Cables.pdf | 29 | Physical Dimensions table
oman-100479 | Needs review | Weight not plausible: Weight of 500 kg/km is less than the conductors alone (about 3,402 kg/km), so it is not used. | Oman Cables | 2-core 630 mm² | Al/XLPE/SWA | 0.6/1 kV | IEC 60502-1 | page 55 | 79 | 500 | Oman Cables.pdf | 55 | Physical Dimensions table
oman-100426 | Needs review | Weight not plausible: Weight of 1,000 kg/km equals the drum length; the columns were probably mixed up, so it is not used. | Oman Cables | 3-core 35 mm² | Al/XLPE/SWA | 0.6/1 kV | IEC 60502-1 | page 55 | 25 | 1000 | Oman Cables.pdf | 55 | Physical Dimensions table
oman-100057 | Needs review | Conductor may be aluminium: Weight of 1,794 kg/km is too light for copper conductors (about 3,200 kg/km) but fits aluminium (about 972 kg/km); the conductor may be aluminium. | Oman Cables | 3-core 120 mm² | Cu/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 23 | 33 | 1794 | Oman Cables.pdf | 23 | Physical Dimensions table
oman-100062 | Needs review | Conductor may be aluminium: Weight of 2,222 kg/km is too light for copper conductors (about 4,001 kg/km) but fits aluminium (about 1,215 kg/km); the conductor may be aluminium. | Oman Cables | 3-core 150 mm² | Cu/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 23 | 37 | 2222 | Oman Cables.pdf | 23 | Physical Dimensions table
oman-100843 | Needs review | Conductor may be aluminium: Weight of 3,169 kg/km is too light for copper conductors (about 4,001 kg/km) but fits aluminium (about 1,215 kg/km); the conductor may be aluminium. | Oman Cables | 3-core 150 mm² | Cu/XLPE/AWA | 1.8/3 kV | IEC 60502-1 | page 107 | 47 | 3169 | Oman Cables.pdf | 107 | Physical Dimensions table
oman-100067 | Needs review | Conductor may be aluminium: Weight of 2,752 kg/km is too light for copper conductors (about 4,934 kg/km) but fits aluminium (about 1,499 kg/km); the conductor may be aluminium. | Oman Cables | 3-core 185 mm² | Cu/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 23 | 39.5 | 2752 | Oman Cables.pdf | 23 | Physical Dimensions table
oman-100845 | Needs review | Conductor may be aluminium: Weight of 3,734 kg/km is too light for copper conductors (about 4,934 kg/km) but fits aluminium (about 1,499 kg/km); the conductor may be aluminium. | Oman Cables | 3-core 185 mm² | Cu/XLPE/AWA | 1.8/3 kV | IEC 60502-1 | page 107 | 49 | 3734 | Oman Cables.pdf | 107 | Physical Dimensions table
oman-100911 | Needs review | Conductor may be aluminium: Weight of 3,895 kg/km is too light for copper conductors (about 4,934 kg/km) but fits aluminium (about 1,499 kg/km); the conductor may be aluminium. | Oman Cables | 3-core 185 mm² | Cu/PVC/AWA | 1.8/3 kV | IEC 60502-1 | page 125 | 50 | 3895 | Oman Cables.pdf | 125 | Physical Dimensions table
oman-100072 | Needs review | Conductor may be aluminium: Weight of 3,589 kg/km is too light for copper conductors (about 6,401 kg/km) but fits aluminium (about 1,944 kg/km); the conductor may be aluminium. | Oman Cables | 3-core 240 mm² | Cu/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 23 | 46 | 3589 | Oman Cables.pdf | 23 | Physical Dimensions table
oman-100847 | Needs review | Conductor may be aluminium: Weight of 4,683 kg/km is too light for copper conductors (about 6,401 kg/km) but fits aluminium (about 1,944 kg/km); the conductor may be aluminium. | Oman Cables | 3-core 240 mm² | Cu/XLPE/AWA | 1.8/3 kV | IEC 60502-1 | page 107 | 55 | 4683 | Oman Cables.pdf | 107 | Physical Dimensions table
oman-100913 | Needs review | Conductor may be aluminium: Weight of 4,872 kg/km is too light for copper conductors (about 6,401 kg/km) but fits aluminium (about 1,944 kg/km); the conductor may be aluminium. | Oman Cables | 3-core 240 mm² | Cu/PVC/AWA | 1.8/3 kV | IEC 60502-1 | page 125 | 56 | 4872 | Oman Cables.pdf | 125 | Physical Dimensions table
oman-100077 | Needs review | Conductor may be aluminium: Weight of 4,483 kg/km is too light for copper conductors (about 8,001 kg/km) but fits aluminium (about 2,430 kg/km); the conductor may be aluminium. | Oman Cables | 3-core 300 mm² | Cu/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 23 | 51.5 | 4483 | Oman Cables.pdf | 23 | Physical Dimensions table
oman-100849 | Needs review | Conductor may be aluminium: Weight of 5,679 kg/km is too light for copper conductors (about 8,001 kg/km) but fits aluminium (about 2,430 kg/km); the conductor may be aluminium. | Oman Cables | 3-core 300 mm² | Cu/XLPE/AWA | 1.8/3 kV | IEC 60502-1 | page 107 | 60 | 5679 | Oman Cables.pdf | 107 | Physical Dimensions table
oman-100915 | Needs review | Conductor may be aluminium: Weight of 2,975 kg/km is too light for copper conductors (about 8,001 kg/km) but fits aluminium (about 2,430 kg/km); the conductor may be aluminium. | Oman Cables | 3-core 300 mm² | Cu/PVC/AWA | 1.8/3 kV | IEC 60502-1 | page 125 | 62 | 2975 | Oman Cables.pdf | 125 | Physical Dimensions table
oman-100939 | Needs review | Weight not plausible: Weight of 1,579 kg/km is less than the conductors alone (about 2,430 kg/km), so it is not used. | Oman Cables | 3-core 300 mm² | Al/PVC/AWA | 1.8/3 kV | IEC 60502-1 | page 131 | 62 | 1579 | Oman Cables.pdf | 131 | Physical Dimensions table
oman-100082 | Needs review | Conductor may be aluminium: Weight of 5,730 kg/km is too light for copper conductors (about 10,668 kg/km) but fits aluminium (about 3,240 kg/km); the conductor may be aluminium. | Oman Cables | 3-core 400 mm² | Cu/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 23 | 56 | 5730 | Oman Cables.pdf | 23 | Physical Dimensions table
oman-100851 | Needs review | Conductor may be aluminium: Weight of 3,487 kg/km is too light for copper conductors (about 10,668 kg/km) but fits aluminium (about 3,240 kg/km); the conductor may be aluminium. | Oman Cables | 3-core 400 mm² | Cu/XLPE/AWA | 1.8/3 kV | IEC 60502-1 | page 107 | 63.5 | 3487 | Oman Cables.pdf | 107 | Physical Dimensions table
oman-100875 | Needs review | Weight not plausible: Weight of 1,686 kg/km is less than the conductors alone (about 3,240 kg/km), so it is not used. | Oman Cables | 3-core 400 mm² | Al/XLPE/AWA | 1.8/3 kV | IEC 60502-1 | page 113 | 63.5 | 1686 | Oman Cables.pdf | 113 | Physical Dimensions table
oman-100917 | Needs review | Conductor may be aluminium: Weight of 3,827 kg/km is too light for copper conductors (about 10,668 kg/km) but fits aluminium (about 3,240 kg/km); the conductor may be aluminium. | Oman Cables | 3-core 400 mm² | Cu/PVC/AWA | 1.8/3 kV | IEC 60502-1 | page 125 | 67.5 | 3827 | Oman Cables.pdf | 125 | Physical Dimensions table
oman-100941 | Needs review | Weight not plausible: Weight of 2,026 kg/km is less than the conductors alone (about 3,240 kg/km), so it is not used. | Oman Cables | 3-core 400 mm² | Al/PVC/AWA | 1.8/3 kV | IEC 60502-1 | page 131 | 67.5 | 2026 | Oman Cables.pdf | 131 | Physical Dimensions table
oman-100087 | Needs review | Conductor may be aluminium: Weight of 3,677 kg/km is too light for copper conductors (about 13,335 kg/km) but fits aluminium (about 4,050 kg/km); the conductor may be aluminium. | Oman Cables | 3-core 500 mm² | Cu/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 23 | 62 | 3677 | Oman Cables.pdf | 23 | Physical Dimensions table
oman-100157 | Needs review | Weight not plausible: Weight of 500 kg/km is less than the conductors alone (about 4,050 kg/km), so it is not used. | Oman Cables | 3-core 500 mm² | Al/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 29 | 73 | 500 | Oman Cables.pdf | 29 | Physical Dimensions table
oman-100476 | Needs review | Weight not plausible: Weight of 250 kg/km is less than the conductors alone (about 4,050 kg/km), so it is not used. | Oman Cables | 3-core 500 mm² | Al/XLPE/SWA | 0.6/1 kV | IEC 60502-1 | page 55 | 83 | 250 | Oman Cables.pdf | 55 | Physical Dimensions table
oman-100092 | Needs review | Conductor may be aluminium: Weight of 6,292 kg/km is too light for copper conductors (about 16,802 kg/km) but fits aluminium (about 5,103 kg/km); the conductor may be aluminium. | Oman Cables | 3-core 630 mm² | Cu/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 23 | 69.5 | 6292 | Oman Cables.pdf | 23 | Physical Dimensions table
oman-100162 | Needs review | Weight not plausible: Weight of 250 kg/km is less than the conductors alone (about 5,103 kg/km), so it is not used. | Oman Cables | 3-core 630 mm² | Al/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 29 | 82 | 250 | Oman Cables.pdf | 29 | Physical Dimensions table
oman-100480 | Needs review | Weight not plausible: Weight of 250 kg/km is less than the conductors alone (about 5,103 kg/km), so it is not used. | Oman Cables | 3-core 630 mm² | Al/XLPE/SWA | 0.6/1 kV | IEC 60502-1 | page 55 | 92 | 250 | Oman Cables.pdf | 55 | Physical Dimensions table
oman-100277 | Needs review | Weight not plausible: Weight of 1,000 kg/km equals the drum length; the columns were probably mixed up, so it is not used. | Oman Cables | 4-core 50 mm² | Al/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 41 | 27.5 | 1000 | Oman Cables.pdf | 41 | Physical Dimensions table
oman-100053 | Needs review | Conductor may be aluminium: Weight of 1,891 kg/km is too light for copper conductors (about 3,378 kg/km) but fits aluminium (about 1,026 kg/km); the conductor may be aluminium. | Oman Cables | 4-core 95 mm² | Cu/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 23 | 33.5 | 1891 | Oman Cables.pdf | 23 | Physical Dimensions table
oman-100535 | Needs review | Conductor may be aluminium: Weight of 1,000 kg/km is too light for copper conductors (about 3,378 kg/km) but fits aluminium (about 1,026 kg/km); the conductor may be aluminium. | Oman Cables | 4-core 95 mm² | Cu/XLPE/SWA | 0.6/1 kV | BS 5467 | page 61 | 39.5 | 1000 | Oman Cables.pdf | 61 | Physical Dimensions table
oman-100058 | Needs review | Conductor may be aluminium: Weight of 2,384 kg/km is too light for copper conductors (about 4,267 kg/km) but fits aluminium (about 1,296 kg/km); the conductor may be aluminium. | Oman Cables | 4-core 120 mm² | Cu/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 23 | 39 | 2384 | Oman Cables.pdf | 23 | Physical Dimensions table
oman-100540 | Needs review | Weight not plausible: Weight of 1,000 kg/km is less than the conductors alone (about 4,267 kg/km), so it is not used. | Oman Cables | 4-core 120 mm² | Cu/XLPE/SWA | 0.6/1 kV | BS 5467 | page 61 | 46 | 1000 | Oman Cables.pdf | 61 | Physical Dimensions table
oman-100063 | Needs review | Conductor may be aluminium: Weight of 2,942 kg/km is too light for copper conductors (about 5,334 kg/km) but fits aluminium (about 1,620 kg/km); the conductor may be aluminium. | Oman Cables | 4-core 150 mm² | Cu/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 23 | 43 | 2942 | Oman Cables.pdf | 23 | Physical Dimensions table
oman-100545 | Needs review | Weight not plausible: Weight of 1,000 kg/km is less than the conductors alone (about 5,334 kg/km), so it is not used. | Oman Cables | 4-core 150 mm² | Cu/XLPE/SWA | 0.6/1 kV | BS 5467 | page 61 | 50 | 1000 | Oman Cables.pdf | 61 | Physical Dimensions table
oman-100068 | Needs review | Conductor may be aluminium: Weight of 3,666 kg/km is too light for copper conductors (about 6,579 kg/km) but fits aluminium (about 1,998 kg/km); the conductor may be aluminium. | Oman Cables | 4-core 185 mm² | Cu/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 23 | 48 | 3666 | Oman Cables.pdf | 23 | Physical Dimensions table
oman-100550 | Needs review | Weight not plausible: Weight of 1,000 kg/km is less than the conductors alone (about 6,579 kg/km), so it is not used. | Oman Cables | 4-core 185 mm² | Cu/XLPE/SWA | 0.6/1 kV | BS 5467 | page 61 | 55.5 | 1000 | Oman Cables.pdf | 61 | Physical Dimensions table
oman-100073 | Needs review | Conductor may be aluminium: Weight of 4,767 kg/km is too light for copper conductors (about 8,534 kg/km) but fits aluminium (about 2,592 kg/km); the conductor may be aluminium. | Oman Cables | 4-core 240 mm² | Cu/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 23 | 53.5 | 4767 | Oman Cables.pdf | 23 | Physical Dimensions table
oman-100555 | Needs review | Weight not plausible: Weight of 1,000 kg/km is less than the conductors alone (about 8,534 kg/km), so it is not used. | Oman Cables | 4-core 240 mm² | Cu/XLPE/SWA | 0.6/1 kV | BS 5467 | page 61 | 61 | 1000 | Oman Cables.pdf | 61 | Physical Dimensions table
oman-100078 | Needs review | Conductor may be aluminium: Weight of 5,948 kg/km is too light for copper conductors (about 10,668 kg/km) but fits aluminium (about 3,240 kg/km); the conductor may be aluminium. | Oman Cables | 4-core 300 mm² | Cu/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 23 | 59 | 5948 | Oman Cables.pdf | 23 | Physical Dimensions table
oman-100560 | Needs review | Weight not plausible: Weight of 500 kg/km is less than the conductors alone (about 10,668 kg/km), so it is not used. | Oman Cables | 4-core 300 mm² | Cu/XLPE/SWA | 0.6/1 kV | BS 5467 | page 61 | 66.5 | 500 | Oman Cables.pdf | 61 | Physical Dimensions table
oman-100083 | Needs review | Conductor may be aluminium: Weight of 3,811 kg/km is too light for copper conductors (about 14,224 kg/km) but fits aluminium (about 4,320 kg/km); the conductor may be aluminium. | Oman Cables | 4-core 400 mm² | Cu/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 23 | 67.5 | 3811 | Oman Cables.pdf | 23 | Physical Dimensions table
oman-100565 | Needs review | Weight not plausible: Weight of 500 kg/km is less than the conductors alone (about 14,224 kg/km), so it is not used. | Oman Cables | 4-core 400 mm² | Cu/XLPE/SWA | 0.6/1 kV | BS 5467 | page 61 | 76.5 | 500 | Oman Cables.pdf | 61 | Physical Dimensions table
oman-100088 | Needs review | Conductor may be aluminium: Weight of 4,884 kg/km is too light for copper conductors (about 17,780 kg/km) but fits aluminium (about 5,400 kg/km); the conductor may be aluminium. | Oman Cables | 4-core 500 mm² | Cu/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 23 | 73 | 4884 | Oman Cables.pdf | 23 | Physical Dimensions table
oman-100252 | Needs review | Weight not plausible: Weight of 500 kg/km is less than the conductors alone (about 17,780 kg/km), so it is not used. | Oman Cables | 4-core 500 mm² | Cu/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 35 | 76 | 500 | Oman Cables.pdf | 35 | Physical Dimensions table
oman-100407 | Needs review | Weight not plausible: Weight of 500 kg/km is less than the conductors alone (about 17,780 kg/km), so it is not used. | Oman Cables | 4-core 500 mm² | Cu/XLPE/SWA | 0.6/1 kV | IEC 60502-1 | page 49 | 82.5 | 500 | Oman Cables.pdf | 49 | Physical Dimensions table
oman-100655 | Needs review | Weight not plausible: Weight of 500 kg/km is less than the conductors alone (about 17,780 kg/km), so it is not used. | Oman Cables | 4-core 500 mm² | Cu/PVC/SWA | 0.6/1 kV | IEC 60502-1 | page 67 | 85.5 | 500 | Oman Cables.pdf | 67 | Physical Dimensions table
oman-100725 | Needs review | Weight not plausible: Weight of 500 kg/km is less than the conductors alone (about 5,400 kg/km), so it is not used. | Oman Cables | 4-core 500 mm² | Al/PVC/SWA | 0.6/1 kV | IEC 60502-1 | page 73 | 85.5 | 500 | Oman Cables.pdf | 73 | Physical Dimensions table
oman-100158 | Needs review | Weight not plausible: Weight of 250 kg/km is less than the conductors alone (about 5,400 kg/km), so it is not used. | Oman Cables | 4-core 500 mm² | Al/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 29 | 90 | 250 | Oman Cables.pdf | 29 | Physical Dimensions table
oman-100093 | Needs review | Weight not plausible: Weight of 500 kg/km is less than the conductors alone (about 22,403 kg/km), so it is not used. | Oman Cables | 4-core 630 mm² | Cu/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 23 | 82 | 500 | Oman Cables.pdf | 23 | Physical Dimensions table
oman-100257 | Needs review | Weight not plausible: Weight of 500 kg/km is less than the conductors alone (about 22,403 kg/km), so it is not used. | Oman Cables | 4-core 630 mm² | Cu/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 35 | 84 | 500 | Oman Cables.pdf | 35 | Physical Dimensions table
oman-100412 | Needs review | Weight not plausible: Weight of 500 kg/km is less than the conductors alone (about 22,403 kg/km), so it is not used. | Oman Cables | 4-core 630 mm² | Cu/XLPE/SWA | 0.6/1 kV | IEC 60502-1 | page 49 | 92 | 500 | Oman Cables.pdf | 49 | Physical Dimensions table
oman-100660 | Needs review | Weight not plausible: Weight of 500 kg/km is less than the conductors alone (about 22,403 kg/km), so it is not used. | Oman Cables | 4-core 630 mm² | Cu/PVC/SWA | 0.6/1 kV | IEC 60502-1 | page 67 | 94 | 500 | Oman Cables.pdf | 67 | Physical Dimensions table
oman-100730 | Needs review | Weight not plausible: Weight of 500 kg/km is less than the conductors alone (about 6,804 kg/km), so it is not used. | Oman Cables | 4-core 630 mm² | Al/PVC/SWA | 0.6/1 kV | IEC 60502-1 | page 73 | 94 | 500 | Oman Cables.pdf | 73 | Physical Dimensions table
oman-100506 | Needs review | Weight not plausible: Weight of 1,000 kg/km equals the drum length; the columns were probably mixed up, so it is not used. | Oman Cables | 5-core 10 mm² | Cu/XLPE/SWA | 0.6/1 kV | BS 5467 | page 61 | 21.5 | 1000 | Oman Cables.pdf | 61 | Physical Dimensions table
oman-100343 | Needs review | Weight not plausible: Weight of 1,000 kg/km equals the drum length; the columns were probably mixed up, so it is not used. | Oman Cables | 5-core 10 mm² | Cu/XLPE/SWA | 0.6/1 kV | IEC 60502-1 | page 49 | 22.5 | 1000 | Oman Cables.pdf | 49 | Physical Dimensions table
oman-100044 | Needs review | Conductor may be aluminium: Weight of 1,292 kg/km is too light for copper conductors (about 2,223 kg/km) but fits aluminium (about 675 kg/km); the conductor may be aluminium. | Oman Cables | 5-core 50 mm² | Cu/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 23 | 31.5 | 1292 | Oman Cables.pdf | 23 | Physical Dimensions table
oman-100049 | Needs review | Conductor may be aluminium: Weight of 1,813 kg/km is too light for copper conductors (about 3,112 kg/km) but fits aluminium (about 945 kg/km); the conductor may be aluminium. | Oman Cables | 5-core 70 mm² | Cu/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 23 | 36.5 | 1813 | Oman Cables.pdf | 23 | Physical Dimensions table
oman-100054 | Needs review | Conductor may be aluminium: Weight of 2,486 kg/km is too light for copper conductors (about 4,223 kg/km) but fits aluminium (about 1,283 kg/km); the conductor may be aluminium. | Oman Cables | 5-core 95 mm² | Cu/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 23 | 41.5 | 2486 | Oman Cables.pdf | 23 | Physical Dimensions table
oman-100059 | Needs review | Conductor may be aluminium: Weight of 3,127 kg/km is too light for copper conductors (about 5,334 kg/km) but fits aluminium (about 1,620 kg/km); the conductor may be aluminium. | Oman Cables | 5-core 120 mm² | Cu/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 23 | 46 | 3127 | Oman Cables.pdf | 23 | Physical Dimensions table
oman-100064 | Needs review | Conductor may be aluminium: Weight of 3,843 kg/km is too light for copper conductors (about 6,668 kg/km) but fits aluminium (about 2,025 kg/km); the conductor may be aluminium. | Oman Cables | 5-core 150 mm² | Cu/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 23 | 51 | 3843 | Oman Cables.pdf | 23 | Physical Dimensions table
oman-100069 | Needs review | Conductor may be aluminium: Weight of 4,803 kg/km is too light for copper conductors (about 8,223 kg/km) but fits aluminium (about 2,498 kg/km); the conductor may be aluminium. | Oman Cables | 5-core 185 mm² | Cu/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 23 | 57 | 4803 | Oman Cables.pdf | 23 | Physical Dimensions table
oman-100074 | Needs review | Conductor may be aluminium: Weight of 3,130 kg/km is too light for copper conductors (about 10,668 kg/km) but fits aluminium (about 3,240 kg/km); the conductor may be aluminium. | Oman Cables | 5-core 240 mm² | Cu/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 23 | 64 | 3130 | Oman Cables.pdf | 23 | Physical Dimensions table
oman-100079 | Needs review | Conductor may be aluminium: Weight of 3,903 kg/km is too light for copper conductors (about 13,335 kg/km) but fits aluminium (about 4,050 kg/km); the conductor may be aluminium. | Oman Cables | 5-core 300 mm² | Cu/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 23 | 71 | 3903 | Oman Cables.pdf | 23 | Physical Dimensions table
oman-100084 | Needs review | Conductor may be aluminium: Weight of 4,963 kg/km is too light for copper conductors (about 17,780 kg/km) but fits aluminium (about 5,400 kg/km); the conductor may be aluminium. | Oman Cables | 5-core 400 mm² | Cu/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 23 | 80.5 | 4963 | Oman Cables.pdf | 23 | Physical Dimensions table
oman-100089 | Needs review | Conductor may be aluminium: Weight of 6,336 kg/km is too light for copper conductors (about 22,225 kg/km) but fits aluminium (about 6,750 kg/km); the conductor may be aluminium. | Oman Cables | 5-core 500 mm² | Cu/XLPE/Unarmoured | 0.6/1 kV | IEC 60502-1 | page 23 | 90 | 6336 | Oman Cables.pdf | 23 | Physical Dimensions table
riyadh-399 | Excluded | Impossible OD: OD of 6.0 mm is smaller than the conductors of a 4-core 15 mm² cable (typically 13.1–31.5 mm). Non-standard size: 15 mm² is not a standard conductor size; the size was probably misread. Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. | Riyadh Cables | 4-core 15 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page | 6 | 45 | Riyadh cables.pdf |  | 4x15 re 1 1.38 o7 14 6 45 1000
riyadh-401 | Excluded | Impossible OD: OD of 6.0 mm is smaller than the conductors of a 4-core 25 mm² cable (typically 16.9–40.6 mm). Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. | Riyadh Cables | 4-core 25 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page | 6 | 60 | Riyadh cables.pdf |  | 4x25 re 1 178 o7 14 6 60 4000
riyadh-408 | Excluded | Impossible OD: OD of 13.0 mm is smaller than the conductors of a 4-core 35 mm² cable (typically 18.7–37.4 mm). Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. | Riyadh Cables | 4-core 35 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page | 13 | 400 | Riyadh cables.pdf |  | 4x35 rm 7 7.44 09 14 13 400 1000
riyadh-405 | Excluded | Impossible OD: OD of 9.0 mm is smaller than the conductors of a 4-core 40 mm² cable (typically 20.0–40.0 mm). Non-standard size: 40 mm² is not a standard conductor size; the size was probably misread. Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. | Riyadh Cables | 4-core 40 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page | 9 | 145 | Riyadh cables.pdf |  | 4x40 1m 7 401 o7 14 9 145 1000
riyadh-409 | Excluded | Impossible OD: OD of 14.0 mm is smaller than the conductors of a 4-core 50 mm² cable (typically 22.3–44.7 mm). Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. | Riyadh Cables | 4-core 50 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page | 14 | 525 | Riyadh cables.pdf |  | 4x50. rm 19 88 10 14 “ 525 1000
riyadh-355 | Excluded | Impossible OD: OD of 7.0 mm is smaller than the conductors of a 4-core 70 mm² cable (typically 26.4–52.9 mm). Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Weight not plausible: Weight of 375 kg/km is more than a solid copper rod of this OD, so it is not used. | Riyadh Cables | 4-core 70 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page | 7 | 375 | Riyadh cables.pdf |  | 4x70, rm 19 10.55 14 14 "7 375 1000
riyadh-410 | Excluded | Impossible OD: OD of 16.0 mm is smaller than the conductors of a 4-core 70 mm² cable (typically 26.4–52.9 mm). Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. | Riyadh Cables | 4-core 70 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page | 16 | 725 | Riyadh cables.pdf |  | 4x70 em 19 106 14 14 16 725 1000
riyadh-477 | Excluded | Impossible OD: OD of 16.0 mm is smaller than the conductors of a 4-core 70 mm² cable (typically 26.4–52.9 mm). Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. | Riyadh Cables | 4-core 70 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page | 16 | 325 | Riyadh cables.pdf |  | 4x70 em 19 10.55 14 14 16 325 4000
riyadh-411 | Excluded | Impossible OD: OD of 18.0 mm is smaller than the conductors of a 4-core 95 mm² cable (typically 30.1–50.6 mm). Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. | Riyadh Cables | 4-core 95 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page | 18 | 1000 | Riyadh cables.pdf |  | 4x95 rm 19 124 44 15 18 1000 1000
riyadh-478 | Excluded | Impossible OD: OD of 18.0 mm is smaller than the conductors of a 4-core 95 mm² cable (typically 30.1–50.6 mm). Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. | Riyadh Cables | 4-core 95 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page | 18 | 425 | Riyadh cables.pdf |  | 4x95 rm 19 124 14 18 18 425 1000
riyadh-356 | Excluded | Impossible OD: OD of 19.0 mm is smaller than the conductors of a 4-core 95 mm² cable (typically 30.1–50.6 mm). Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. | Riyadh Cables | 4-core 95 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page | 19 | 500 | Riyadh cables.pdf |  | 4x95. rm 19 12.40 1.6 15 19 500 1000
riyadh-357 | Excluded | Impossible OD: OD of 15.0 mm is smaller than the conductors of a 4-core 120 mm² cable (typically 33.9–56.9 mm). Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. | Riyadh Cables | 4-core 120 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page | 15 | 600 | Riyadh cables.pdf |  | 4x120. rm 37 14,00 16 15 a 600 1000
riyadh-412 | Excluded | Impossible OD: OD of 20.0 mm is smaller than the conductors of a 4-core 120 mm² cable (typically 33.9–56.9 mm). Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. | Riyadh Cables | 4-core 120 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page | 20 | 1225 | Riyadh cables.pdf |  | 4x120. rm 37 140 12 15 20 1225 1000
riyadh-508 | Excluded | Impossible OD: OD of 24.0 mm is smaller than the conductors of a 4-core 150 mm² cable (typically 37.9–63.6 mm). Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. | Riyadh Cables | 4-core 150 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page | 24 | 2675 | Riyadh cables.pdf |  | 4x150 sm 15 - 14 24 ar 2675 500
riyadh-413 | Excluded | Impossible OD: OD of 24.0 mm is smaller than the conductors of a 4-core 185 mm² cable (typically 42.1–70.6 mm). Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. | Riyadh Cables | 4-core 185 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page | 24 | 1875 | Riyadh cables.pdf |  | 4x185 rm 37 174 16 16 24 1875 1000
riyadh-414 | Excluded | Impossible OD: OD of 17.0 mm is smaller than the conductors of a 4-core 240 mm² cable (typically 47.9–80.4 mm). Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Weight not plausible: Weight of 2,450 kg/km is more than a solid copper rod of this OD, so it is not used. | Riyadh Cables | 4-core 240 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page | 17 | 2450 | Riyadh cables.pdf |  | 4x240 em 61 20.0 17 17 ar 2450 4000
riyadh-360 | Excluded | Impossible OD: OD of 28.0 mm is smaller than the conductors of a 4-core 240 mm² cable (typically 47.9–80.4 mm). Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. | Riyadh Cables | 4-core 240 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page | 28 | 1150 | Riyadh cables.pdf |  | 4x240 rm e 19.89 z2 18 28 1150 1000
riyadh-415 | Excluded | Impossible OD: OD of 30.0 mm is smaller than the conductors of a 4-core 300 mm² cable (typically 54.3–82.1 mm). Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. | Riyadh Cables | 4-core 300 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page | 30 | 3050 | Riyadh cables.pdf |  | 4x300 rm 61 225 18 18 30 3050 1000
riyadh-480 | Excluded | Impossible OD: OD of 30.0 mm is smaller than the conductors of a 4-core 300 mm² cable (typically 54.3–82.1 mm). Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. | Riyadh Cables | 4-core 300 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page | 30 | 1200 | Riyadh cables.pdf |  | 4x300 rm 6 22.2 18 18 30 1200 1000
riyadh-416 | Excluded | Impossible OD: OD of 34.0 mm is smaller than the conductors of a 4-core 400 mm² cable (typically 62.7–94.8 mm). Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. | Riyadh Cables | 4-core 400 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page | 34 | 3900 | Riyadh cables.pdf |  | 4x400 rm 61 254 20 19 34 3900 500
riyadh-482 | Excluded | Impossible OD: OD of 37.0 mm is smaller than the conductors of a 4-core 500 mm² cable (typically 70.1–106.0 mm). Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. | Riyadh Cables | 4-core 500 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page | 37 | 1925 | Riyadh cables.pdf |  | 4x500_ em et 286 ve: 20 37 1925 500
riyadh-417 | Excluded | Impossible OD: OD of 42.0 mm is smaller than the conductors of a 4-core 630 mm² cable (typically 78.7–119.0 mm). Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. | Riyadh Cables | 4-core 630 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page | 42 | 6425 | Riyadh cables.pdf |  | 4x630_ rm a1 328 24 22 42 6425 500
riyadh-402 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 14.0 mm is larger than 8.0 mm for the larger 6 mm² size in the same product range. | Riyadh Cables | 1-core 4 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page | 14 | 75 | Riyadh cables.pdf |  | 1x4 re 1 2.25 o7 14 @ 75 1000
riyadh-404 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 8.0 mm is smaller than 14.0 mm for the smaller 4 mm² size in the same product range. OD out of size order: OD of 8.0 mm is larger than 6.0 mm for the larger 15 mm² size in the same product range. Look-alike rows, no code: Same specification as other rows with OD 14.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 1-core 6 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 404 | 8 | 400 | Riyadh cables.pdf |  | 1x6 rm 7 3.12 o7 14 8 400 1000
riyadh-403 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 14.0 mm is larger than 6.0 mm for the larger 15 mm² size in the same product range. Look-alike rows, no code: Same specification as other rows with OD 8.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 1-core 6 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 403 | 14 | 95 | Riyadh cables.pdf |  | 1x6 re 1 276 o7 14 i 95 1000
riyadh-400 | Needs review | Non-standard size: 15 mm² is not a standard conductor size; the size was probably misread. Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 6.0 mm is smaller than 14.0 mm for the smaller 6 mm² size in the same product range. | Riyadh Cables | 1-core 15 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page | 6 | 50 | Riyadh cables.pdf |  | 1x15 1m 7 156 o7 14 6 50 1000
riyadh-475 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. | Riyadh Cables | 1-core 35 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page | 12 | 200 | Riyadh cables.pdf |  | 1x35 rm 7 TAL 09 14 12 200 1000
riyadh-479 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Look-alike rows, no code: Same specification as other rows with OD 23.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 1-core 150 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 479 | 22 | 650 | Riyadh cables.pdf |  | 1x150 rm 37 155 14 16 22 650 1000
riyadh-358 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Look-alike rows, no code: Same specification as other rows with OD 22.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 1-core 150 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 358 | 23 | 725 | Riyadh cables.pdf |  | 1x150 em 37 15.47 18 16 23 725 1000
riyadh-359 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. | Riyadh Cables | 1-core 185 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page | 25 | 900 | Riyadh cables.pdf |  | 1x185 rm 37 17.36 20 17 25 900 1000
riyadh-362 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. | Riyadh Cables | 1-core 400 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page | 35 | 1750 | Riyadh cables.pdf |  | 1x400 rm 61 25.20 26 20 35 1750 500
riyadh-483 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Look-alike rows, no code: Same specification as other rows with OD 43.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 1-core 630 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 483 | 42 | 2475 | Riyadh cables.pdf |  | 1x630 rm oO 32.6 24 22 42 2475 500
riyadh-363 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Look-alike rows, no code: Same specification as other rows with OD 42.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 1-core 630 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 363 | 43 | 2725 | Riyadh cables.pdf |  | 1x630 rm 1 32.56 28 22 43 2725 500
riyadh-419 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Weight not plausible: Weight of 275 kg/km is more than a solid copper rod of this OD, so it is not used. | Riyadh Cables | 2-core 4 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page | 4 | 275 | Riyadh cables.pdf |  | 2x4 rm 7 255 o7 18 “4 275 1000
riyadh-420 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 16.0 mm is larger than 7.0 mm for the larger 10 mm² size in the same product range. | Riyadh Cables | 2-core 6 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page | 16 | 350 | Riyadh cables.pdf |  | 2x6 rm 7 3.2 o7 18 16 350 1000
riyadh-421 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Weight not plausible: Weight of 475 kg/km is more than a solid copper rod of this OD, so it is not used. OD out of size order: OD of 7.0 mm is smaller than 16.0 mm for the smaller 6 mm² size in the same product range. | Riyadh Cables | 2-core 10 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page | 7 | 475 | Riyadh cables.pdf |  | 2x10 rm 2 401 o7 18 7 475 1000
riyadh-418 | Needs review | Non-standard size: 15 mm² is not a standard conductor size; the size was probably misread. Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. | Riyadh Cables | 2-core 15 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page | 13 | 200 | Riyadh cables.pdf |  | 2x15 1m 7 1.56 o7 18 13 200 1000
riyadh-422 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Look-alike rows, no code: Same specification as other rows with OD 20.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 2-core 16 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 422 | 19 | 650 | Riyadh cables.pdf |  | 2x16 rm 7 5.03 o7 18 19 650 1000
riyadh-364 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Look-alike rows, no code: Same specification as other rows with OD 19.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 2-core 16 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 364 | 20 | 525 | Riyadh cables.pdf |  | 2x16 1m 7 4.98 1.0 18 20 525 4000
riyadh-423 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. | Riyadh Cables | 2-core 25 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page | 23 | 925 | Riyadh cables.pdf |  | 2x25 rm 7 63 09 18 23 925 1000
riyadh-484 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. | Riyadh Cables | 2-core 25 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page | 23 | 625 | Riyadh cables.pdf |  | 2x25 rm ¦ 7 6.30 09 1.8 23 625 1000,
riyadh-424 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Look-alike rows, no code: Same specification as other rows with OD 26.0, 25.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 2-core 35 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 424 | 25 | 1200 | Riyadh cables.pdf |  | 2x35 rm 7 744 09 18 25 1200 1000
riyadh-485 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Look-alike rows, no code: Same specification as other rows with OD 26.0, 25.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 2-core 35 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 485 | 25 | 775 | Riyadh cables.pdf |  | 2x35 rm 7 71 09 18 25 775 1000
riyadh-365 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Look-alike rows, no code: Same specification as other rows with OD 25.0, 25.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 2-core 35 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 365 | 26 | 875 | Riyadh cables.pdf |  | 2x35 rm 7 Tat 12 18 26 875 1000
riyadh-426 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 13.0 mm is larger than 4.0 mm for the larger 4 mm² size in the same product range. | Riyadh Cables | 3-core 1.5 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page | 13 | 210 | Riyadh cables.pdf |  | 3x1.5 rm 7 156 o7 18 13 210 1000
riyadh-428 | Needs review | Unusual OD: OD of 4.0 mm is unusual for a 3-core 4 mm² cable (typically 4.9–22.7 mm). Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Weight not plausible: Weight of 325 kg/km is more than a solid copper rod of this OD, so it is not used. OD out of size order: OD of 4.0 mm is smaller than 13.0 mm for the smaller 1.5 mm² size in the same product range. Look-alike rows, no code: Same specification as other rows with OD 18.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 4 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 428 | 4 | 325 | Riyadh cables.pdf |  | 3x4. te 1 225 or 18 “4 325 4000
riyadh-429 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 18.0 mm is larger than 16.0 mm for the larger 6 mm² size in the same product range. Look-alike rows, no code: Same specification as other rows with OD 4.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 4 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 429 | 18 | 325 | Riyadh cables.pdf |  | 3x4 rm 7 255 o7 18 18 325 1000
riyadh-431 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 16.0 mm is smaller than 18.0 mm for the smaller 4 mm² size in the same product range. Look-alike rows, no code: Same specification as other rows with OD 18.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 6 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 431 | 16 | 400 | Riyadh cables.pdf |  | 3x6 rm 7 3.12 7 18 16 400 1000
riyadh-430 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Look-alike rows, no code: Same specification as other rows with OD 16.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 6 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 430 | 18 | 400 | Riyadh cables.pdf |  | 3x6 re 1 276 o7 18 18 400 1000
riyadh-432 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 18.0 mm is larger than 13.0 mm for the larger 15 mm² size in the same product range. Look-alike rows, no code: Same specification as other rows with OD 48.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 10 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 432 | 18 | 575 | Riyadh cables.pdf |  | 3x10 rm 7 401 o7 18 18 575 1000
riyadh-490 | Needs review | Unusual OD: OD of 48.0 mm is unusual for a 3-core 10 mm² cable (typically 8.7–27.2 mm). Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 48.0 mm is larger than 13.0 mm for the larger 15 mm² size in the same product range. Look-alike rows, no code: Same specification as other rows with OD 18.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 10 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 490 | 48 | 5120 | Riyadh cables.pdf |  | 3x10. rm 37 185 14 23 48 5120 500
riyadh-425 | Needs review | Non-standard size: 15 mm² is not a standard conductor size; the size was probably misread. Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 13.0 mm is smaller than 48.0 mm for the smaller 10 mm² size in the same product range. | Riyadh Cables | 3-core 15 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page | 13 | 200 | Riyadh cables.pdf |  | 3x15 re 1 1.38 o7 18 13 200 4000
riyadh-433 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 20.0 mm is larger than 14.0 mm for the larger 25 mm² size in the same product range. Look-alike rows, no code: Same specification as other rows with OD 22.0, 20.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 16 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 433 | 20 | 800 | Riyadh cables.pdf |  | 3x16 rm 7 5.03 o7 18 20 800 1000
riyadh-486 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 20.0 mm is larger than 14.0 mm for the larger 25 mm² size in the same product range. Look-alike rows, no code: Same specification as other rows with OD 22.0, 20.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 16 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 486 | 20 | 500 | Riyadh cables.pdf |  | 3x16 rm 7 50 o7 18 20 500 4000
riyadh-366 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 22.0 mm is larger than 14.0 mm for the larger 25 mm² size in the same product range. Look-alike rows, no code: Same specification as other rows with OD 20.0, 20.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 16 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 366 | 22 | 600 | Riyadh cables.pdf |  | 3x16 im 7 4.98 10 18 22 600 4000
riyadh-427 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 14.0 mm is smaller than 22.0 mm for the smaller 16 mm² size in the same product range. Look-alike rows, no code: Same specification as other rows with OD 25.0, 18.0, 28.0, 25.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 25 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 427 | 14 | 275 | Riyadh cables.pdf |  | 3x25 rm 7 201 o7 18 14 275 1000
riyadh-377 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 18.0 mm is smaller than 22.0 mm for the smaller 16 mm² size in the same product range. Look-alike rows, no code: Same specification as other rows with OD 25.0, 14.0, 28.0, 25.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 25 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 377 | 18 | 200 | Riyadh cables.pdf |  | 3x25 mis. ¦ 7 ¦ 7¦ 63 ¦ 498) 12 ¦ 1.0 18 ar 200 1000
riyadh-367 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Look-alike rows, no code: Same specification as other rows with OD 18.0, 14.0, 28.0, 25.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 25 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 367 | 25 | 825 | Riyadh cables.pdf |  | 3x25 rm 7 6.30 12 18 25 825 1000
riyadh-446 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Look-alike rows, no code: Same specification as other rows with OD 25.0, 18.0, 14.0, 28.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 25 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 446 | 25 | 1925 | Riyadh cables.pdf |  | 3x25 rms ¦ 7 ¦ 7 ¦ 630 ¦ 503¦ 09 ¦ a7 18 25 1925 1000
riyadh-434 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Look-alike rows, no code: Same specification as other rows with OD 25.0, 18.0, 14.0, 25.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 25 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 434 | 28 | 1150 | Riyadh cables.pdf |  | 3x25 rm 2 63 09 18 28 1150 1000
riyadh-499 | Needs review | Unusual OD: OD of 61.0 mm is unusual for a 3-core 30 mm² cable (typically 16.1–38.5 mm). Non-standard size: 30 mm² is not a standard conductor size; the size was probably misread. Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 61.0 mm is larger than 18.0 mm for the larger 35 mm² size in the same product range. | Riyadh Cables | 3-core 30 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page | 61 | 4650 | Riyadh cables.pdf |  | 3x30 sm+150] 30 37] - ¦ 1547] 1.8 ¦ 14 29 61 4650 250
riyadh-378 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 18.0 mm is smaller than 61.0 mm for the smaller 30 mm² size in the same product range. Look-alike rows, no code: Same specification as other rows with OD 28.0, 27.0, 25.0, 26.0, 25.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 35 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 378 | 18 | 875 | Riyadh cables.pdf |  | 3x35 sme ¦ 6 ¦ 7 ¦ - ¦ 498] 12 ¦ 10 18 ar 875 1000
riyadh-447 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 25.0 mm is smaller than 61.0 mm for the smaller 30 mm² size in the same product range. Look-alike rows, no code: Same specification as other rows with OD 28.0, 18.0, 27.0, 26.0, 25.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 35 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 447 | 25 | 1475 | Riyadh cables.pdf |  | 3x35 sme ¦ 6 ¦ 7 ¦ - ¦ 503¦ 09 ¦ 07 18 25 1475 1000
riyadh-495 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 25.0 mm is smaller than 61.0 mm for the smaller 30 mm² size in the same product range. Look-alike rows, no code: Same specification as other rows with OD 28.0, 18.0, 27.0, 25.0, 26.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 35 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 495 | 25 | 750 | Riyadh cables.pdf |  | 3x35 sme ¦ 6 ¦ 7 ¦ - ¦ 498¦ 09 ¦ o7 18 25 750 1000
riyadh-487 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 26.0 mm is smaller than 61.0 mm for the smaller 30 mm² size in the same product range. Look-alike rows, no code: Same specification as other rows with OD 28.0, 18.0, 27.0, 25.0, 25.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 35 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 487 | 26 | 750 | Riyadh cables.pdf |  | 3x35. rm i 741 09 18 26 750 1000
riyadh-435 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 27.0 mm is smaller than 61.0 mm for the smaller 30 mm² size in the same product range. Look-alike rows, no code: Same specification as other rows with OD 28.0, 18.0, 25.0, 26.0, 25.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 35 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 435 | 27 | 1375 | Riyadh cables.pdf |  | 3x35 rm 7 744 09 18 27 1375 1000
riyadh-368 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 28.0 mm is smaller than 61.0 mm for the smaller 30 mm² size in the same product range. Look-alike rows, no code: Same specification as other rows with OD 18.0, 27.0, 25.0, 26.0, 25.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 35 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 368 | 28 | 875 | Riyadh cables.pdf |  | 3x35 rm 7 7a 12 18 28 875 1000
riyadh-444 | Needs review | Unusual OD: OD of 74.0 mm is unusual for a 3-core 40 mm² cable (typically 17.3–34.6 mm). Non-standard size: 40 mm² is not a standard conductor size; the size was probably misread. Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 74.0 mm is larger than 18.0 mm for the larger 50 mm² size in the same product range. | Riyadh Cables | 3-core 40 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page | 74 | 13050 | Riyadh cables.pdf |  | 3x40 rm 61 25.38 20 34 74 13050 250
riyadh-369 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 18.0 mm is smaller than 74.0 mm for the smaller 40 mm² size in the same product range. Look-alike rows, no code: Same specification as other rows with OD 85.0, 31.0, 30.0, 83.0, 30.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 50 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 369 | 18 | 1100 | Riyadh cables.pdf |  | 3x50. rm 19 875 14 18 a1 1100 500
riyadh-436 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 30.0 mm is smaller than 74.0 mm for the smaller 40 mm² size in the same product range. OD out of size order: OD of 30.0 mm is larger than 20.0 mm for the larger 70 mm² size in the same product range. Look-alike rows, no code: Same specification as other rows with OD 18.0, 85.0, 31.0, 83.0, 30.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 50 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 436 | 30 | 1800 | Riyadh cables.pdf |  | 3x50 rm 19 88 10 18 30 1800 4000
riyadh-488 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 30.0 mm is smaller than 74.0 mm for the smaller 40 mm² size in the same product range. OD out of size order: OD of 30.0 mm is larger than 20.0 mm for the larger 70 mm² size in the same product range. Look-alike rows, no code: Same specification as other rows with OD 18.0, 85.0, 31.0, 30.0, 83.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 50 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 488 | 30 | 1785 | Riyadh cables.pdf |  | 3x50 rm 19 88 1.0 18 30 1785, 500
riyadh-379 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 31.0 mm is smaller than 74.0 mm for the smaller 40 mm² size in the same product range. OD out of size order: OD of 31.0 mm is larger than 20.0 mm for the larger 70 mm² size in the same product range. Look-alike rows, no code: Same specification as other rows with OD 18.0, 85.0, 30.0, 83.0, 30.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 50 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 379 | 31 | 1150 | Riyadh cables.pdf |  | 3x50 sm+25 6 i x 63 14 1.2 1.9 31 1150 500,
riyadh-445 | Needs review | Unusual OD: OD of 83.0 mm is unusual for a 3-core 50 mm² cable (typically 19.3–38.7 mm). Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 83.0 mm is larger than 20.0 mm for the larger 70 mm² size in the same product range. Look-alike rows, no code: Same specification as other rows with OD 18.0, 85.0, 31.0, 30.0, 30.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 50 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 445 | 83 | 16625 | Riyadh cables.pdf |  | 3x50 rm 61 28.8 22 33 83 16625 250
riyadh-376 | Needs review | Unusual OD: OD of 85.0 mm is unusual for a 3-core 50 mm² cable (typically 19.3–38.7 mm). Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 85.0 mm is larger than 20.0 mm for the larger 70 mm² size in the same product range. Look-alike rows, no code: Same specification as other rows with OD 18.0, 31.0, 30.0, 83.0, 30.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 50 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 376 | 85 | 8350 | Riyadh cables.pdf |  | 3x50. rm. 61 28.62 28 34 85 8350 250
riyadh-380 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 20.0 mm is smaller than 85.0 mm for the smaller 50 mm² size in the same product range. Look-alike rows, no code: Same specification as other rows with OD 36.0, 35.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 70 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 380 | 20 | 1475 | Riyadh cables.pdf |  | 3x70 sm+35. 12 7 af 7.441 14 12 20 uw 1475 500
riyadh-437 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 35.0 mm is smaller than 85.0 mm for the smaller 50 mm² size in the same product range. Look-alike rows, no code: Same specification as other rows with OD 36.0, 20.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 70 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 437 | 35 | 2500 | Riyadh cables.pdf |  | 3x70 1m 19 10.55 4 19 35 2500 500
riyadh-370 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 36.0 mm is smaller than 85.0 mm for the smaller 50 mm² size in the same product range. Look-alike rows, no code: Same specification as other rows with OD 20.0, 35.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 70 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 370 | 36 | 1475 | Riyadh cables.pdf |  | 3x70, rm 19 10.55 14 20 36 1475 500
riyadh-448 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Look-alike rows, no code: Same specification as other rows with OD 39.0, 39.0, 39.0, 37.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 95 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 448 | 37 | 3675 | Riyadh cables.pdf |  | 3x95 sm+50 ¦ 15 ¦ 19) - ¦ 88 ¦ 11 ¦ 10 24 37 3675 500
riyadh-496 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Look-alike rows, no code: Same specification as other rows with OD 39.0, 39.0, 37.0, 39.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 95 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 496 | 37 | 1650 | Riyadh cables.pdf |  | 3x95 sm+so ¦ 15 ¦ 19) - ¦ 875/11 ¦ 10 24 37 1650 500
riyadh-381 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Look-alike rows, no code: Same specification as other rows with OD 39.0, 37.0, 39.0, 37.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 95 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 381 | 39 | 1950 | Riyadh cables.pdf |  | 3x95 sm+50 15 ¦ 19 x 875 ¦ 16 14 22 39 1950 500,
riyadh-438 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Look-alike rows, no code: Same specification as other rows with OD 39.0, 37.0, 39.0, 37.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 95 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 438 | 39 | 3350 | Riyadh cables.pdf |  | 3x95 rm 19 124 14 20 39 3350 500
riyadh-489 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Look-alike rows, no code: Same specification as other rows with OD 39.0, 39.0, 37.0, 37.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 95 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 489 | 39 | 3340 | Riyadh cables.pdf |  | 3x95 rm 19 124 4 20 39 3340 500
riyadh-497 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Look-alike rows, no code: Same specification as other rows with OD 43.0, 43.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 120 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 497 | 40 | 2000 | Riyadh cables.pdf |  | 3x120 sm+70 ¦ 15 ¦ 19} - ¦ 1058) 12 ¦ 1.1 22 40 2000 600
riyadh-382 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Look-alike rows, no code: Same specification as other rows with OD 43.0, 40.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 120 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 382 | 43 | 2375 | Riyadh cables.pdf |  | 3x120 sm+70 ¦ 15] 19] - ¦ 1055] 16 ¦ 14 23 43 2375 500
riyadh-439 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Look-alike rows, no code: Same specification as other rows with OD 43.0, 40.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 120 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 439 | 43 | 4150 | Riyadh cables.pdf |  | 3x120. rm 37 14.0 12 24 43 4150 500
riyadh-371 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 49.0 mm is larger than 48.0 mm for the larger 180 mm² size in the same product range. | Riyadh Cables | 3-core 150 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page | 49 | 275 | Riyadh cables.pdf |  | 3x150_ rm 37 15.47 18 23 49 275 500
riyadh-440 | Needs review | Non-standard size: 180 mm² is not a standard conductor size; the size was probably misread. Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 48.0 mm is smaller than 49.0 mm for the smaller 150 mm² size in the same product range. | Riyadh Cables | 3-core 180 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page | 48 | 5125 | Riyadh cables.pdf |  | 3x180. rm 37 15.47 14 23 48 5125 500
riyadh-383 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Look-alike rows, no code: Same specification as other rows with OD 55.0, 53.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 185 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 383 | 52 | 3450 | Riyadh cables.pdf |  | 3x185 sm+95 ¦ 30 ¦ 19 # 12.4 ¦ 2.0 1.6 26 52 3450 250
riyadh-441 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Look-alike rows, no code: Same specification as other rows with OD 55.0, 52.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 185 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 441 | 53 | 6375 | Riyadh cables.pdf |  | 3x185 rm 37 17.36 16 24 53 6375 250
riyadh-372 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Look-alike rows, no code: Same specification as other rows with OD 52.0, 53.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 185 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 372 | 55 | 3425 | Riyadh cables.pdf |  | 3x185 mm 37 17.36 20 26 55 3425 250
riyadh-449 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Look-alike rows, no code: Same specification as other rows with OD 62.0, 58.0, 60.0, 60.0, 55.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 240 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 449 | 55 | 9275 | Riyadh cables.pdf |  | 3x240 sm+120¦ 34] 37 ¦ - ¦ 140) 17 ¦ 42 27 55 9275 250
riyadh-498 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Look-alike rows, no code: Same specification as other rows with OD 62.0, 58.0, 60.0, 55.0, 60.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 240 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 498 | 55 | 3850 | Riyadh cables.pdf |  | 3x240 sm+120] 30 ¦ 37] - ¦ 140] 17 ¦ 12 27 55 3850 250
riyadh-384 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Look-alike rows, no code: Same specification as other rows with OD 62.0, 60.0, 55.0, 60.0, 55.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 240 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 384 | 58 | 4400 | Riyadh cables.pdf |  | 3x240 sm+120) 30 ¦ 37 * 14.0 ¦ 2.2 16 28 58 4400 250
riyadh-442 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Look-alike rows, no code: Same specification as other rows with OD 62.0, 58.0, 55.0, 60.0, 55.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 240 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 442 | 60 | 8275 | Riyadh cables.pdf |  | 3x240 rm 61 20.25 17 26 60 8275 250
riyadh-491 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Look-alike rows, no code: Same specification as other rows with OD 62.0, 58.0, 60.0, 55.0, 55.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 240 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 491 | 60 | 8280 | Riyadh cables.pdf |  | 3x240 rm. 61 19.9 17 26 60 8280 250
riyadh-373 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 62.0 mm is larger than 61.0 mm for the larger 300 mm² size in the same product range. Look-alike rows, no code: Same specification as other rows with OD 58.0, 60.0, 55.0, 60.0, 55.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 240 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 373 | 62 | 4375 | Riyadh cables.pdf |  | 3x240, erm 61 19.89 22 27 62 4375 250
riyadh-450 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 61.0 mm is smaller than 62.0 mm for the smaller 240 mm² size in the same product range. Look-alike rows, no code: Same specification as other rows with OD 68.0, 64.0, 67.0, 66.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 300 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 450 | 61 | 1180 | Riyadh cables.pdf |  | 3x300 sm+150¦ 34 ¦ 37 ¦ - ¦ 155] 18 ¦ 14 29 61 +1180 250
riyadh-385 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Look-alike rows, no code: Same specification as other rows with OD 68.0, 67.0, 61.0, 66.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 300 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 385 | 64 | 5375 | Riyadh cables.pdf |  | 3x300 sm+150¦ 30 ¦ 37 - 15.47) 2.4 1.8 3.0 64 5375 250
riyadh-492 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Weight not plausible: Weight of 40,270 kg/km is more than a solid copper rod of this OD, so it is not used. Look-alike rows, no code: Same specification as other rows with OD 68.0, 64.0, 67.0, 61.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 300 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 492 | 66 | 40270 | Riyadh cables.pdf |  | 3x300 rm 61 222 18 28 66 40270 250
riyadh-443 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Look-alike rows, no code: Same specification as other rows with OD 68.0, 64.0, 61.0, 66.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 300 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 443 | 67 | 10275 | Riyadh cables.pdf |  | 3x300_ rm 61 22.68 18 28 67 10275 250
riyadh-374 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Look-alike rows, no code: Same specification as other rows with OD 64.0, 67.0, 61.0, 66.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 300 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 374 | 68 | 5325 | Riyadh cables.pdf |  | 3x300 rm 61 22.23 24 29 68 5325 250
riyadh-451 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Weight not plausible: Weight of 44,500 kg/km is more than a solid copper rod of this OD, so it is not used. Look-alike rows, no code: Same specification as other rows with OD 76.0, 74.0, 68.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 400 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 451 | 68 | 44500 | Riyadh cables.pdf |  | 3x400 sm+tes¦ 53] 37 ¦ - ¦ 174¦ 20 ¦ 16 34 68 44500 250
riyadh-500 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Look-alike rows, no code: Same specification as other rows with OD 76.0, 68.0, 74.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 400 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 500 | 68 | 5875 | Riyadh cables.pdf |  | 3x400 sm+ta5¦ 53 ¦ 37¦ - ¦ 17.36¦ 20 ¦ 16 34 68 5875 250
riyadh-493 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Look-alike rows, no code: Same specification as other rows with OD 76.0, 68.0, 68.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 400 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 493 | 74 | 13040 | Riyadh cables.pdf |  | 3x400 rm 61 25.2 2.0 3.4 74 13040 250
riyadh-375 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Look-alike rows, no code: Same specification as other rows with OD 68.0, 74.0, 68.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 400 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 375 | 76 | 6675 | Riyadh cables.pdf |  | 3x400 em 61 252 26 34 76 6675 250
riyadh-452 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Look-alike rows, no code: Same specification as other rows with OD 83.0, 76.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 500 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 452 | 76 | 18050 | Riyadh cables.pdf |  | 3x500 sm+240¦ 63} 61 ¦ - ¦ 200¦ 22 ¦ 17 34 76 18050 250
riyadh-501 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Look-alike rows, no code: Same specification as other rows with OD 76.0, 83.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 500 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 501 | 76 | 7425 | Riyadh cables.pdf |  | 3x500 sm+240¦ 53 ¦ 61¦ - ¦ 1989] 22 ¦ 17 34 76 7425 250
riyadh-494 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Look-alike rows, no code: Same specification as other rows with OD 76.0, 76.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 3-core 500 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 494 | 83 | 16610 | Riyadh cables.pdf |  | 3x500. rm et 286 22 33 83 16610 250
riyadh-455 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. | Riyadh Cables | 4-core 2.5 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page | 15 | 300 | Riyadh cables.pdf |  | 4x2.5 rm cs 2.01 o7 18 15 300 1000,
riyadh-456 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 15.0 mm is larger than 7.0 mm for the larger 6 mm² size in the same product range. Look-alike rows, no code: Same specification as other rows with OD 16.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 4-core 4 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 456 | 15 | 375 | Riyadh cables.pdf |  | 4x4 ro 1 225 07 18 15 375 4000
riyadh-457 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 16.0 mm is larger than 7.0 mm for the larger 6 mm² size in the same product range. Look-alike rows, no code: Same specification as other rows with OD 15.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 4-core 4 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 457 | 16 | 400 | Riyadh cables.pdf |  | 4x4 rm ig 2.55 O7 18 16 400 1000
riyadh-459 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Weight not plausible: Weight of 500 kg/km is more than a solid copper rod of this OD, so it is not used. OD out of size order: OD of 7.0 mm is smaller than 16.0 mm for the smaller 4 mm² size in the same product range. Look-alike rows, no code: Same specification as other rows with OD 17.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 4-core 6 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 459 | 7 | 500 | Riyadh cables.pdf |  | 4x6 1m 7 312 07 18 7 500 1000
riyadh-458 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Look-alike rows, no code: Same specification as other rows with OD 7.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 4-core 6 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 458 | 17 | 475 | Riyadh cables.pdf |  | 4x6 re 1 276 O7 18 17 475 1000
riyadh-460 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 20.0 mm is larger than 13.0 mm for the larger 15 mm² size in the same product range. | Riyadh Cables | 4-core 10 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page | 20 | 700 | Riyadh cables.pdf |  | 4x10 1m 7 401 07 18 20 700 4000
riyadh-453 | Needs review | Non-standard size: 15 mm² is not a standard conductor size; the size was probably misread. Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 13.0 mm is smaller than 20.0 mm for the smaller 10 mm² size in the same product range. OD out of size order: OD of 13.0 mm is larger than 10.0 mm for the larger 16 mm² size in the same product range. Look-alike rows, no code: Same specification as other rows with OD 14.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 4-core 15 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 453 | 13 | 230 | Riyadh cables.pdf |  | 4x15 re 1 1.38 07 18 13 230 1000
riyadh-454 | Needs review | Non-standard size: 15 mm² is not a standard conductor size; the size was probably misread. Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 14.0 mm is smaller than 20.0 mm for the smaller 10 mm² size in the same product range. OD out of size order: OD of 14.0 mm is larger than 10.0 mm for the larger 16 mm² size in the same product range. Look-alike rows, no code: Same specification as other rows with OD 13.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 4-core 15 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 454 | 14 | 250 | Riyadh cables.pdf |  | 4x15 rm 7 156 07 18 14 250 1000
riyadh-352 | Needs review | Unusual OD: OD of 10.0 mm is unusual for a 4-core 16 mm² cable (typically 13.5–32.5 mm). Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 10.0 mm is smaller than 14.0 mm for the smaller 15 mm² size in the same product range. Look-alike rows, no code: Same specification as other rows with OD 10.0, 40.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 4-core 16 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 352 | 10 | 135 | Riyadh cables.pdf |  | 4x16 rm Zi 4.98 1.0 14 10 135 1000
riyadh-406 | Needs review | Unusual OD: OD of 10.0 mm is unusual for a 4-core 16 mm² cable (typically 13.5–32.5 mm). Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 10.0 mm is smaller than 14.0 mm for the smaller 15 mm² size in the same product range. Look-alike rows, no code: Same specification as other rows with OD 10.0, 40.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 4-core 16 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 406 | 10 | 200 | Riyadh cables.pdf |  | 4x16 em 7 5.03 o7 14 10 200 1000
riyadh-473 | Needs review | Unusual OD: OD of 40.0 mm is unusual for a 4-core 16 mm² cable (typically 13.5–32.5 mm). Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 40.0 mm is larger than 14.0 mm for the larger 25 mm² size in the same product range. Look-alike rows, no code: Same specification as other rows with OD 10.0, 10.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 4-core 16 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 473 | 40 | 110 | Riyadh cables.pdf |  | 4x16 rm a 50 07 14 40 110 1000
riyadh-407 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 14.0 mm is smaller than 40.0 mm for the smaller 16 mm² size in the same product range. Look-alike rows, no code: Same specification as other rows with OD 28.0, 26.0, 14.0, 26.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 4-core 25 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 407 | 14 | 300 | Riyadh cables.pdf |  | 4x25 rm 7 63 09 14 " 300 4000
riyadh-474 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 14.0 mm is smaller than 40.0 mm for the smaller 16 mm² size in the same product range. Look-alike rows, no code: Same specification as other rows with OD 28.0, 14.0, 26.0, 26.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 4-core 25 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 474 | 14 | 150 | Riyadh cables.pdf |  | 4x25 rm 7 6.30 09 14 " 150 1000
riyadh-461 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 26.0 mm is smaller than 40.0 mm for the smaller 16 mm² size in the same product range. Look-alike rows, no code: Same specification as other rows with OD 28.0, 14.0, 14.0, 26.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 4-core 25 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 461 | 26 | 1450 | Riyadh cables.pdf |  | 4x25 ™m 7 63 09 18 26 1450 1000
riyadh-502 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 26.0 mm is smaller than 40.0 mm for the smaller 16 mm² size in the same product range. Look-alike rows, no code: Same specification as other rows with OD 28.0, 14.0, 26.0, 14.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 4-core 25 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 502 | 26 | 850 | Riyadh cables.pdf |  | 4x25 1m 7 6.30 09 18 26 850 1000
riyadh-387 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 28.0 mm is smaller than 40.0 mm for the smaller 16 mm² size in the same product range. Look-alike rows, no code: Same specification as other rows with OD 14.0, 26.0, 14.0, 26.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 4-core 25 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 387 | 28 | 1000 | Riyadh cables.pdf |  | 4x25 1m z 6.30 12 18 28 1000 1000
riyadh-361 | Needs review | Non-standard size: 30 mm² is not a standard conductor size; the size was probably misread. Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 31.0 mm is larger than 26.0 mm for the larger 35 mm² size in the same product range. | Riyadh Cables | 4-core 30 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page | 31 | 1400 | Riyadh cables.pdf |  | 4x30. rm 61 22.23 24 19 31 1400 500
riyadh-462 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 26.0 mm is smaller than 31.0 mm for the smaller 30 mm² size in the same product range. Look-alike rows, no code: Same specification as other rows with OD 28.0, 26.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 4-core 35 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 462 | 26 | 1650 | Riyadh cables.pdf |  | 4x35 sm 6 E 09 18 26 1650 1000
riyadh-503 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 26.0 mm is smaller than 31.0 mm for the smaller 30 mm² size in the same product range. Look-alike rows, no code: Same specification as other rows with OD 28.0, 26.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 4-core 35 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 503 | 26 | 800 | Riyadh cables.pdf |  | 4x35 sm 6 - 09 18 26 800 1000
riyadh-388 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 28.0 mm is smaller than 31.0 mm for the smaller 30 mm² size in the same product range. Look-alike rows, no code: Same specification as other rows with OD 26.0, 26.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 4-core 35 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 388 | 28 | 925 | Riyadh cables.pdf |  | 4x35 sm 6 S 4.2 1.8 28 925 1000
riyadh-481 | Needs review | Non-standard size: 40 mm² is not a standard conductor size; the size was probably misread. Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 33.0 mm is larger than 23.0 mm for the larger 46 mm² size in the same product range. Look-alike rows, no code: Same specification as other rows with OD 73.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 4-core 40 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 481 | 33 | 1525 | Riyadh cables.pdf |  | 4x40 rm 6 25.2 20 19 33 1525 500
riyadh-512 | Needs review | Unusual OD: OD of 73.0 mm is unusual for a 4-core 40 mm² cable (typically 20.0–40.0 mm). Non-standard size: 40 mm² is not a standard conductor size; the size was probably misread. Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 73.0 mm is larger than 23.0 mm for the larger 46 mm² size in the same product range. Look-alike rows, no code: Same specification as other rows with OD 33.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 4-core 40 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 512 | 73 | 6550 | Riyadh cables.pdf |  | 4x40. sm 53 - 20 3.3 73 6550 250
riyadh-386 | Needs review | Non-standard size: 46 mm² is not a standard conductor size; the size was probably misread. Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 23.0 mm is smaller than 73.0 mm for the smaller 40 mm² size in the same product range. OD out of size order: OD of 23.0 mm is larger than 16.0 mm for the larger 50 mm² size in the same product range. | Riyadh Cables | 4-core 46 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page | 23 | 700 | Riyadh cables.pdf |  | 4x46 1m 7 498 10 18 23 700 1000
riyadh-354 | Needs review | Unusual OD: OD of 16.0 mm is unusual for a 4-core 50 mm² cable (typically 22.3–44.7 mm). Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 16.0 mm is smaller than 23.0 mm for the smaller 46 mm² size in the same product range. Look-alike rows, no code: Same specification as other rows with OD 30.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 4-core 50 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 354 | 16 | 300 | Riyadh cables.pdf |  | 4x50 rm 19 8.75 14 14 16 300 1000
riyadh-504 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Look-alike rows, no code: Same specification as other rows with OD 16.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 4-core 50 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 504 | 30 | 1025 | Riyadh cables.pdf |  | 4x50 sm 6 = 1.0 19 30 1025 1000
riyadh-463 | Needs review | Non-standard size: 60 mm² is not a standard conductor size; the size was probably misread. Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Look-alike rows, no code: Same specification as other rows with OD 32.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 4-core 60 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 463 | 30 | 2175 | Riyadh cables.pdf |  | 4x60 sm 6 E 10 19 30 2175 1000
riyadh-389 | Needs review | Non-standard size: 60 mm² is not a standard conductor size; the size was probably misread. Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Look-alike rows, no code: Same specification as other rows with OD 30.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 4-core 60 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 389 | 32 | 1250 | Riyadh cables.pdf |  | 4x60 sm 6 z 14 19 32 1250 500
riyadh-464 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 34.0 mm is larger than 22.0 mm for the larger 95 mm² size in the same product range. Look-alike rows, no code: Same specification as other rows with OD 36.0, 34.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 4-core 70 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 464 | 34 | 3050 | Riyadh cables.pdf |  | 4x70 sm 12 : 14 20 34 3050 500
riyadh-505 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 34.0 mm is larger than 22.0 mm for the larger 95 mm² size in the same product range. Look-alike rows, no code: Same specification as other rows with OD 36.0, 34.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 4-core 70 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 505 | 34 | 1375 | Riyadh cables.pdf |  | 4x70 sm 2 : 44 20 34 1375 500
riyadh-390 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 36.0 mm is larger than 22.0 mm for the larger 95 mm² size in the same product range. Look-alike rows, no code: Same specification as other rows with OD 34.0, 34.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 4-core 70 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 390 | 36 | 1600 | Riyadh cables.pdf |  | 4x70 sm 12 : 14 24 36 1600 500
riyadh-391 | Needs review | Unusual OD: OD of 22.0 mm is unusual for a 4-core 95 mm² cable (typically 30.1–50.6 mm). Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 22.0 mm is smaller than 36.0 mm for the smaller 70 mm² size in the same product range. Look-alike rows, no code: Same specification as other rows with OD 38.0, 38.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 4-core 95 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 391 | 22 | 2100 | Riyadh cables.pdf |  | 4x95 sm 18 ia 16 22 ay 2100 500
riyadh-465 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Look-alike rows, no code: Same specification as other rows with OD 22.0, 38.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 4-core 95 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 465 | 38 | 4100 | Riyadh cables.pdf |  | 4x95 sm 15 = 441 24 38 4100 500
riyadh-506 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Look-alike rows, no code: Same specification as other rows with OD 22.0, 38.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 4-core 95 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 506 | 38 | 4775 | Riyadh cables.pdf |  | 4x95 sm 15 - 14 24 38 4775 500
riyadh-466 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Look-alike rows, no code: Same specification as other rows with OD 45.0, 43.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 4-core 120 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 466 | 43 | 5125 | Riyadh cables.pdf |  | 4x120 sm 18 : 12 23 43 5125 500
riyadh-507 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Look-alike rows, no code: Same specification as other rows with OD 45.0, 43.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 4-core 120 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 507 | 43 | 2200 | Riyadh cables.pdf |  | 4x120 sm 15 : 12 23 43 2200 500
riyadh-392 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Look-alike rows, no code: Same specification as other rows with OD 43.0, 43.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 4-core 120 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 392 | 45 | 2550 | Riyadh cables.pdf |  | 4x120 sm 15 a 16 24 45 2550 500
riyadh-467 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Look-alike rows, no code: Same specification as other rows with OD 49.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 4-core 150 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 467 | 47 | 6300 | Riyadh cables.pdf |  | 4x150 sm 18 - 14 24 47 6300 500
riyadh-393 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Look-alike rows, no code: Same specification as other rows with OD 47.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 4-core 150 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 393 | 49 | 3075 | Riyadh cables.pdf |  | 4x150 sm 18 : 18 25 49 3075 500
riyadh-468 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Look-alike rows, no code: Same specification as other rows with OD 55.0, 52.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 4-core 185 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 468 | 52 | 7825 | Riyadh cables.pdf |  | 4x185 sm 30 E 16 26 52 7825 250
riyadh-509 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Look-alike rows, no code: Same specification as other rows with OD 55.0, 52.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 4-core 185 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 509 | 52 | 3275 | Riyadh cables.pdf |  | 4x185 sm 30 : 16 26 52 3275 250
riyadh-394 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Look-alike rows, no code: Same specification as other rows with OD 52.0, 52.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 4-core 185 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 394 | 55 | 3800 | Riyadh cables.pdf |  | 4x185 sm 30 5 20 27 55 3800 250
riyadh-469 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Look-alike rows, no code: Same specification as other rows with OD 61.0, 58.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 4-core 240 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 469 | 58 | 10150 | Riyadh cables.pdf |  | 4x240 sm 34 - AT 28 58 10150 250
riyadh-510 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Look-alike rows, no code: Same specification as other rows with OD 61.0, 58.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 4-core 240 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 510 | 58 | 4225 | Riyadh cables.pdf |  | 4x240 sm 30 - 17 28 58 4225 250
riyadh-395 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Look-alike rows, no code: Same specification as other rows with OD 58.0, 58.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 4-core 240 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 395 | 61 | 4825 | Riyadh cables.pdf |  | 4x240 sm 30 5 22 29 61 4825 250
riyadh-470 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Look-alike rows, no code: Same specification as other rows with OD 87.0, 64.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 4-core 300 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 470 | 64 | 12575 | Riyadh cables.pdf |  | 4x300 sm 34 : 18 30 64 12575 250
riyadh-511 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. Look-alike rows, no code: Same specification as other rows with OD 87.0, 64.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 4-core 300 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 511 | 64 | 5100 | Riyadh cables.pdf |  | 4x300 sm 30 : 18 3.0 64 5100 250
riyadh-396 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 87.0 mm is larger than 73.0 mm for the larger 400 mm² size in the same product range. Look-alike rows, no code: Same specification as other rows with OD 64.0, 64.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 4-core 300 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 396 | 87 | 5875 | Riyadh cables.pdf |  | 4x300 sm 30 : 24 34 87 5875 250
riyadh-471 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 73.0 mm is smaller than 87.0 mm for the smaller 300 mm² size in the same product range. Look-alike rows, no code: Same specification as other rows with OD 76.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 4-core 400 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 471 | 73 | 16075 | Riyadh cables.pdf |  | 4x400 sm 53 - 2.0 33 73 16075 250
riyadh-397 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. OD out of size order: OD of 76.0 mm is smaller than 87.0 mm for the smaller 300 mm² size in the same product range. Look-alike rows, no code: Same specification as other rows with OD 73.0 mm, and no product code or page to tell them apart. | Riyadh Cables | 4-core 400 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page · row 397 | 76 | 7875 | Riyadh cables.pdf |  | 4x400 sm 53 7 26 34 76 7875 250
riyadh-472 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. | Riyadh Cables | 4-core 500 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page | 80 | 20375 | Riyadh cables.pdf |  | 4x500 sm 53 : 22 38 80 20375 250
riyadh-513 | Needs review | Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. | Riyadh Cables | 4-core 500 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page | 80 | 8175 | Riyadh cables.pdf |  | 4x500 sm 53 - 22 35 80 8175 250
riyadh-398 | Needs review | Non-standard size: 600 mm² is not a standard conductor size; the size was probably misread. Conductor missing: Conductor material (copper or aluminium) is missing from the catalogue data. | Riyadh Cables | 4-core 600 mm² | ?/PVC/Unarmoured | 0.6/1 kV | IEC 60502-1 | no code or page | 83 | 9225 | Riyadh cables.pdf |  | 4x600 sm 53 5 28 36 83 9225 250
saudi-1938 | Needs review | Look-alike rows, no code: Same specification as other rows with OD 13.7 mm, and no product code or page to tell them apart. | Saudi Cable Company | 3-core 1.5 mm² | Cu/PVC/STA | 0.6/1 kV | IEC 60502-1 | page 23 · row 13_1938 | 13.6 | 262 | Saudi cables.pdf | 23 | 1.5 7 0.8 0.2 1.8 13.6 262 1000
saudi-1946 | Needs review | Look-alike rows, no code: Same specification as other rows with OD 13.6 mm, and no product code or page to tell them apart. | Saudi Cable Company | 3-core 1.5 mm² | Cu/PVC/STA | 0.6/1 kV | IEC 60502-1 | page 23 · row 13_1946 | 13.7 | 272 | Saudi cables.pdf | 23 | 1.5rm 7 0.8 0.2 1.8 13.7 272 1000
saudi-1939 | Needs review | Look-alike rows, no code: Same specification as other rows with OD 14.6 mm, and no product code or page to tell them apart. | Saudi Cable Company | 3-core 2.5 mm² | Cu/PVC/STA | 0.6/1 kV | IEC 60502-1 | page 23 · row 13_1939 | 14.5 | 301 | Saudi cables.pdf | 23 | 2.5 7 0.8 0.2 1.8 14.5 301 1000
saudi-1947 | Needs review | Look-alike rows, no code: Same specification as other rows with OD 14.5 mm, and no product code or page to tell them apart. | Saudi Cable Company | 3-core 2.5 mm² | Cu/PVC/STA | 0.6/1 kV | IEC 60502-1 | page 23 · row 13_1947 | 14.6 | 319 | Saudi cables.pdf | 23 | 2.5rm 7 0.8 0.2 1.8 14.6 319 1000
saudi-1940 | Needs review | Look-alike rows, no code: Same specification as other rows with OD 16.6 mm, and no product code or page to tell them apart. | Saudi Cable Company | 3-core 4 mm² | Cu/PVC/STA | 0.6/1 kV | IEC 60502-1 | page 23 · row 13_1940 | 16.5 | 358 | Saudi cables.pdf | 23 | 4 7 1 0.2 1.8 16.5 358 1000
saudi-1948 | Needs review | Look-alike rows, no code: Same specification as other rows with OD 16.5 mm, and no product code or page to tell them apart. | Saudi Cable Company | 3-core 4 mm² | Cu/PVC/STA | 0.6/1 kV | IEC 60502-1 | page 23 · row 13_1948 | 16.6 | 418 | Saudi cables.pdf | 23 | 4rm 7 1 0.2 1.8 16.6 418 1000
saudi-1949 | Needs review | Look-alike rows, no code: Same specification as other rows with OD 17.8, 18.0 mm, and no product code or page to tell them apart. | Saudi Cable Company | 3-core 6 mm² | Cu/PVC/STA | 0.6/1 kV | IEC 60502-1 | page 23 · row 13_1949 | 17.5 | 500 | Saudi cables.pdf | 23 | 6sd 1 1 0.2 1.8 17.5 500 1000
saudi-1941 | Needs review | Look-alike rows, no code: Same specification as other rows with OD 17.5, 18.0 mm, and no product code or page to tell them apart. | Saudi Cable Company | 3-core 6 mm² | Cu/PVC/STA | 0.6/1 kV | IEC 60502-1 | page 23 · row 13_1941 | 17.8 | 457 | Saudi cables.pdf | 23 | 6 7 1 0.2 1.8 17.8 457 1000
saudi-1950 | Needs review | Look-alike rows, no code: Same specification as other rows with OD 17.8, 17.5 mm, and no product code or page to tell them apart. | Saudi Cable Company | 3-core 6 mm² | Cu/PVC/STA | 0.6/1 kV | IEC 60502-1 | page 23 · row 13_1950 | 18 | 507 | Saudi cables.pdf | 23 | 6rm 7 1 0.2 1.8 18 507 1000
saudi-1951 | Needs review | Look-alike rows, no code: Same specification as other rows with OD 19.3, 19.5 mm, and no product code or page to tell them apart. | Saudi Cable Company | 3-core 10 mm² | Cu/PVC/STA | 0.6/1 kV | IEC 60502-1 | page 23 · row 13_1951 | 19.2 | 650 | Saudi cables.pdf | 23 | 10sd 1 1 0.2 1.8 19.2 650 1000
saudi-1942 | Needs review | Look-alike rows, no code: Same specification as other rows with OD 19.2, 19.5 mm, and no product code or page to tell them apart. | Saudi Cable Company | 3-core 10 mm² | Cu/PVC/STA | 0.6/1 kV | IEC 60502-1 | page 23 · row 13_1942 | 19.3 | 571 | Saudi cables.pdf | 23 | 10 7 1 0.2 1.8 19.3 571 1000
saudi-1952 | Needs review | Look-alike rows, no code: Same specification as other rows with OD 19.3, 19.2 mm, and no product code or page to tell them apart. | Saudi Cable Company | 3-core 10 mm² | Cu/PVC/STA | 0.6/1 kV | IEC 60502-1 | page 23 · row 13_1952 | 19.5 | 656 | Saudi cables.pdf | 23 | 10rm 7 1 0.2 1.8 19.5 656 1000
saudi-2027 | Needs review | Weight not plausible: Weight of 184 kg/km is less than the conductors alone (about 933 kg/km), so it is not used. | Saudi Cable Company | 3-core 35 mm² | Cu/PVC/SWA | 0.6/1 kV | IEC 60502-1 | page 29 | 27.8 | 184 | Saudi cables.pdf | 29 | 35sm 6 1.2 1.25 1.8 27.8 184 500
saudi-1968 | Needs review | OD out of size order: OD of 18.9 mm is larger than 18.3 mm for the larger 6 mm² size in the same product range. | Saudi Cable Company | 4-core 4 mm² | Cu/PVC/STA | 0.6/1 kV | IEC 60502-1 | page 25 | 18.9 | 474 | Saudi cables.pdf | 25 | 4rm 7 1 0.2 1.8 18.9 474 1000
saudi-1969 | Needs review | OD out of size order: OD of 18.3 mm is smaller than 18.9 mm for the smaller 4 mm² size in the same product range. Look-alike rows, no code: Same specification as other rows with OD 18.7 mm, and no product code or page to tell them apart. | Saudi Cable Company | 4-core 6 mm² | Cu/PVC/STA | 0.6/1 kV | IEC 60502-1 | page 25 · row 13_1969 | 18.3 | 573 | Saudi cables.pdf | 25 | 6sd 1 1 0.2 1.8 18.3 573 1000
saudi-1970 | Needs review | Look-alike rows, no code: Same specification as other rows with OD 18.3 mm, and no product code or page to tell them apart. | Saudi Cable Company | 4-core 6 mm² | Cu/PVC/STA | 0.6/1 kV | IEC 60502-1 | page 25 · row 13_1970 | 18.7 | 579 | Saudi cables.pdf | 25 | 6rm 7 1 0.2 1.8 18.7 579 1000
saudi-1971 | Needs review | Look-alike rows, no code: Same specification as other rows with OD 20.7 mm, and no product code or page to tell them apart. | Saudi Cable Company | 4-core 10 mm² | Cu/PVC/STA | 0.6/1 kV | IEC 60502-1 | page 25 · row 13_1971 | 20.3 | 770 | Saudi cables.pdf | 25 | 10sd 1 1 0.2 1.8 20.3 770 1000
saudi-1972 | Needs review | Look-alike rows, no code: Same specification as other rows with OD 20.3 mm, and no product code or page to tell them apart. | Saudi Cable Company | 4-core 10 mm² | Cu/PVC/STA | 0.6/1 kV | IEC 60502-1 | page 25 · row 13_1972 | 20.7 | 777 | Saudi cables.pdf | 25 | 10rm 7 1 0.2 1.8 20.7 777 1000

## Already reviewed
Row ID | Decision | Corrected values | Note | Reviewed by | Date
doha-1436 | correct | sizeMm2 = 2.5 | Catalogue text reads "2 .5 rm" and 7.41 ohm/km, the IEC 60228 value for 2.5 mm² copper. | Import fix (catalogue text) | 2026-09-28
doha-1444 | correct | sizeMm2 = 2.5 | Catalogue text reads "2 .5 rm" and 7.41 ohm/km, the IEC 60228 value for 2.5 mm² copper. | Import fix (catalogue text) | 2026-09-28
doha-1692 | correct | sizeMm2 = 2.5 | Catalogue text reads "2 .5 rm" and 7.41 ohm/km, the IEC 60228 value for 2.5 mm² copper. | Import fix (catalogue text) | 2026-09-28
doha-1700 | correct | sizeMm2 = 2.5 | Catalogue text reads "2 .5 rm" and 7.41 ohm/km, the IEC 60228 value for 2.5 mm² copper. | Import fix (catalogue text) | 2026-09-28

## Summary
Brand | Checked | Needs review | Excluded | Total
alfanar | 280 | 27 | 0 | 307
Bahra Electric | 227 | 14 | 0 | 241
Doha Cables | 510 | 0 | 0 | 510
Ducab | 21 | 0 | 0 | 21
Jeddah Cable Company | 16 | 0 | 18 | 34
Oman Cables | 809 | 101 | 32 | 942
RAMCRO | 110 | 0 | 0 | 110
Riyadh Cables | 0 | 138 | 22 | 160
Saudi Cable Company | 112 | 18 | 0 | 130
All | 2085 | 298 | 72 | 2455
Problem | Rows
Conductor missing | 160
Look-alike rows, no code | 130
OD out of size order | 78
Weight not plausible | 77
Conductor may be aluminium | 72
Impossible OD | 72
Core count missing | 17
Non-standard size | 17
Unusual OD | 12